## OVERVIEW
Client | UC Berkeley | Input
Project | Campus energy study update | Lookup
Job Number | 267147 | Calculation
Output
Check
Calculation Overview
This spreadsheet calculates 30-year utility (natural gas, electricity, water, and carbon) projections for the UC Berkeley campus under different campus energy system options. Commodities are calculated for core options (systems that replace cogeneration, such as central heating and cooling) with and without enhancements (optional add-ons such as solar PV and thermal energy storage). The Global Inputs tab contains system-agnostic inputs and assumptions, such as carbon intensity of the grid, constants, conversions, and distribution efficiencies for steam and hot water systems. These values are derived from a number of sources, including UC Berkeley stakeholders, consultant reports, and measured data. These from the Global Inputs tab are used to develop the conversion factors on the Core Inputs tab, which are specific to the individual campus energy systems studied. The conversion factors from the Core Inputs tab are applied to the load projections on the Core Loads. Load profiles were calculated by splitting measured and interpolated campus steam, electricity, and gas usage into its component loads: heating, cooling, process steam, and other electricity. The profiles account for demolition, new construction, implementation of building-level energy conservation measures (ECMs), addition of comfort cooling, and phased transition over time from old to new systems. This calculation was completed in the Load Profiles spreadsheet. Lastly, certain options were evaluated with and without enhancements such as thermal energy storage and solar PV. These enhancements were sized to avoid triggering an upgrade to the Hill Substation. Calculated externally, the amount of energy produced by enhancements is listed in the Enhancement Inputs tab. To convert the load profiles into commodities consumption, the core loads were multipled by the conversion factors on the Core Inputs tab to produce the electricity, natural gas, and water usage on the Core Commodities Use tab. Commodities usage is calculated separately for the old and new systems to account for phased transition over time from old to new systems. Final outputs are shown on the Outputs tab. Outputs are shown for both core options alone (top section) and with enhancements (bottom section), which account for the impacts listed on the Enhancement Inputs tab. A few notes on Outputs: - Phasing varies by option. Options 1a, b, 1c, 8a, 8b, 11a, and 11b are phased assuming surge space is the limiting factor. Options 0, 2, 6, 10a, 11c-E, and 12 have been re-evaluated with "fastest feasible" phasing that assumed ample surge space is construction schedule was the limiting factor. - Costs on the Outputs tab are sourced from the Cost Estimate spreadsheet. - In the comparison tables, the year 2045 is used to show the "after" condition, e.g. system performance after transition from old to new system is complete - Some options (1b, 8a, 11b) are not shown in the summary table. These options were deemed unfeasible due to electrical constraints. To implement these options and retain redundancy would require an upgrade to the Hill Substation and another line from PG&E, which was concluded to be prohibitively time consuming and expensive.

## Global Inputs
Client | UC Berkeley |  |  | Input
Project | Campus energy study update |  |  | Lookup
Job Number | 267147 |  |  | Calculation
Output
Check
Inputs - General
Constants and Conversions
Parameter | Unit | Value | Source
Start year | Year | 2025 | 2015 energy delivery options study
Absorption chiller split | % | 26% | Installed chiller capacity; ratio of absorption to total
Absorption chiller load | ton-hrs/y | 3945989.2758 | Year 1 (assume no new absorption chillers added)
Btu per therm | Btu/therm | 100000 | Conversion
Btu per kBtu | Btu/kBtu | 1000 | Conversion
Btuh per W | Btuh/W | 3.412 | Conversion
Btuh per ton | Btuh/ton | 12000 | Conversion
Enthalpy | Btu/lb | 970 | 2015 energy delivery options study
Gallon per CCF | Gal/CCF | 748.2 | Conversion
Minutes per hour | Min/hr | 60 | Conversion
Ft3 per CCF | ft3/CCF | 100 | Conversion
Steam density | lb/ft3 | 62.424 | https://sciencing.com/convert-gravity-pounds-per-gallon-6367099.html
Water flow | Btuh/F-gpm | 500 | Conversion
Pounds per ton | lb/ton | 2000 | Constant
Assumptions
Equipment | Unit | Existing | Source | New | Source
Losses
Building-level steam | % | 15% | Assumption to convert from steam usage to heating, cooling and process loads. Accounts for steam losses through leaky traps, pipes, etc. From 2015 study | 5% | Assumption
Steam distribution (enthalpy) | % | 37% | Steam data analysis and Integral report. % of overall system loss. From 2015 study | 20% | Assumption
Hot water distribution | % | N/A |  | 3% | New pre-insulated system with leak detection. Integral report used 2%-7%. 2015 study
Chilled water distribution | % | N/A |  | 2% | Assumption for new pre-insulated system with leak detection. 2015 study
Transformers | % | 5% | Assumption | 2% | Assumption
Efficiencies
Building heating system | % | 95% | 2015 study | 95% | Assume same as existing
Cogen turbine | % | 67.3% | Expected from conversion to DLE per data received from Gilbert. | 80% | Assumption
Absorption chiller | COP | 0.4 | Assumption due to lack of sub-metered data. Based on average chiller age and discussion with Mike Stone. 2015 study | N/A
Electric chiller | kW/ton | 1.25 | Assumption due to lack of sub-metered data. Based on average chiller age and discussion with Mike Stone. 2015 study | 0.7 | Based on past projects with high efficiency chilled water plants in similar climate. 2015 study. Chiller + balance of plant (pumps, cooling towers, etc.)
Heat recovery chiller | kW/ton | N/A |  | 1 | Assumption
Natural gas steam boiler | % | N/A |  | 88% | Industry standard for new steam boiler plants
Natural HHW gas boiler | % | N/A |  | 92% | Industry standard for new condensing boiler plants
Electric HHW boiler | % | N/A |  | 99% | Cleaverbrooks instantaneous electric resistance boiler
Heat pump | EER (Btu out/W in) | N/A |  | 10 | Clima cool ASHP
Natural gas point steam generator | % | N/A |  | 86% | Cleaverbrooks boiler efficiency guide
Electric point steam generator |  |  |  | 95%
Heat recovery chiller heating offset | % | N/A |  | 40% | DEF tool, scaled to match calculated consumption
Heat recovery chiller cooling fraction | % | N/A |  | 46% | DEF tool, scaled to match calculated consumption
Water Use
Cooling tower flow rate | gpm/ton | 3 |  | 3 | Rule of thumb (from Rob's spreadsheet)
Cooling tower evaporation, blowdown, and drift | % | 2.165% | Assume 50% higher than new due to less efficient equipment, leaks, etc. | 1.443% | Based on 10F delta T, 3 cooling tower cycles (from Rob's spreadsheet)
Steam distribution loss (water) | % | 20% | Steam data analysis and Integral report. % of overall system loss. From 2015 study | 10% | Assumption
Heating loop delta T | F | N/A |  | 45 | Assumption; usually 40-50F
Heating makeup water | % | N/A |  | 0.1%
Cogen plant loss | % | N/A | Covered by steam distribution loss | 2% | Assumption, plant-level losses only
Energy Use
Cogen electricity production | kWh/y | 170237472 | 2018 measured cogen output | 500000000 | Turbine sized to cover 100% of electricity needs
Cogen steam production | lbs/y | 756124000 | 2018 measured cogen output
Cogen steam production | MMBtu/y | 733440.28 | 2018 measured cogen output
Costs
Parameter | Value | Unit | Source
CO2: natural gas | 0.006723 | tons CO2/therm | Source: https://www.pge.com/includes/docs/pdfs/about/environment/calculator/assumptions.pdf
CO2: electricity | 0 | tons CO2/kWh | CA RPS
Carbon cost | 178.35 | $/ton CO2 | Base rate, ICIS, per Kira, escalated to 2045
Electricity cost | 0.30478 | $/kWh | $0.133 base rate escalated 3.5%/y
Natural gas cost | 2.6616 | $/therm | $1.038 base rate escalated 4.0%/y
Water cost | 49.8277 | $/CCF | $10.75 base fee escalated 7.97%/y
Thermal storage discount | 10% | % | Assumption for peak load shedding
Carbon Emissions
Natural gas | 0.006723 | tons/therm
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity (tons/kWh) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas | 6.723e-05 | tons/kBtu
Electricity | 0 | tons/kBtu

## Core Inputs
Client | UC Berkeley |  | Input
Project | Campus energy study update |  | Lookup
Job Number | 267147 |  | Calculation
Output
Check
Inputs- Core Options
Existing
Parameter | Unit | Value | [5 empty] | Source
Heating |  | Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Campus
Electricity | kWh/MMBh | N/A | N/A | N/A | N/A | N/A | 0 | No electric heat
Natural gas | therms/MMBtu | N/A | N/A | N/A | N/A | N/A | 29.208 | See global inputs
Water | CCF/MMBtu | N/A | N/A | N/A | N/A | N/A | 0.1726 | Vanderweil study (2015)
Cooling
Electricity | kW/ton | N/A | N/A | N/A | N/A | N/A | 1.25 | Existing chillers | `
Natural gas | therms/ton-hr | N/A | N/A | N/A | N/A | N/A | 1.7132 | See global inputs
Water | CCF/ton-hr | N/A | N/A | N/A | N/A | N/A | 0.0052086
Process Steam
Electricity | kWh/lb | N/A | N/A | N/A | N/A | N/A | 0 | No electric process steam
Natural gas | therms/lb | N/A | N/A | N/A | N/A | N/A | 0.028332 | See global inputs
Water | CCF/lb | N/A | N/A | N/A | N/A | N/A | 0.00023558 | See global inputs
Electricity
Electricity | kWh/kWh | N/A | N/A | N/A | N/A | N/A | 105% | See global inputs
Enhancements
Electricity | kWh/y
Natural gas | therms/y
Water | CCF/y
Core Option 0
Parameter | Unit | Value | [5 empty] | Source
Heating |  | Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Campus
Electricity | kWh/MMBh | N/A | N/A | N/A | N/A | N/A | 0 | No electric heat
Natural gas | therms/MMBtu | N/A | N/A | N/A | N/A | N/A | 20.5801 | See global inputs
Water | CCF/MMBtu | N/A | N/A | N/A | N/A | N/A | 0.0863 | Vanderweil study (2015), assume distribution water leakage decreases from 20% to 10%
Cooling
Electricity | kW/ton | N/A | N/A | N/A | N/A | N/A | 1.25 | Existing chillers
Natural gas | therms/ton-hr | N/A | N/A | N/A | N/A | N/A | 1.2071 | See global inputs
Water | CCF/ton-hr | N/A | N/A | N/A | N/A | N/A | 0.0052086
Process Steam
Electricity | kWh/lb | N/A | N/A | N/A | N/A | N/A | 0 | No electric process steam
Natural gas | therms/lb | N/A | N/A | N/A | N/A | N/A | 0.019963 | See global inputs
Water | CCF/lb | N/A | N/A | N/A | N/A | N/A | 0.00018736
Electricity
Electricity | kWh/kWh | N/A | N/A | N/A | N/A | N/A | 105% | See global inputs
Enhancements
Electricity | kWh/y
Natural gas | therms/y
Water | CCF/y
Core Option 1A
Parameter | Unit | Value | [5 empty] | Source
Heating |  | Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Campus
Electricity | kWh/MMBh | 0 | 0 | 0 | 0 | 0 | N/A | No electric heat | Htg_0_kWh_per_MMBtu_campus
Natural gas | therms/MMBtu | 8.4254 | 8.4254 | 8.4254 | 8.4254 | 8.4254 | N/A | See global inputs | Htg_0_therm_per_MMBtu_campus
Water | CCF/MMBtu | 0.0035641 | 0.0035641 | 0.0035641 | 0.0035641 | 0.0035641 | N/A | See global inputs | Htg_0_CCF_per_MMBtu_campus
Cooling
Electricity | kW/ton | 0.838 | 0.838 | 0.838 | 0.838 | 0.838 | N/A | New chillers | Clg_0_kWh_per_ton_campus
Water | CCF/ton-hr | 0.0034724 | 0.0034724 | 0.0034724 | 0.0034724 | 0.0034724 | N/A | See global inputs | Clg_0_CCF_per_ton_campus
Process Steam
Electricity | kWh/lb | 0 | 0 | 0 | 0 | 0 | N/A | No electric process steam | Process_0_kWh_per_lb_campus
Natural gas | therms/lb | 0.011873 | 0.011873 | 0.011873 | 0.011873 | 0.011873 | N/A | See global inputs | Process_0_therm_per_lb_campus
Water | CCF/lb | 0.00016863 | 0.00016863 | 0.00016863 | 0.00016863 | 0.00016863 | N/A |  | Process_0_CCF_per_lb_campus
Electricity
Electricity | kWh/kWh | 105% | 105% | 105% | 105% | 105% | N/A | See global inputs | Elec_0_kWh_per_kWh_campus
Enhancements
Electricity | kWh/y
Natural gas | therms/y
Water | CCF/y
Core Option 1B
Parameter | Unit | Value | [5 empty] | Source
Heating |  | Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Campus
Electricity | kWh/MMBh | 229.4734 | 229.4734 | 229.4734 | 229.4734 | 229.4734 | N/A | See global inputs | Htg_0_kWh_per_MMBtu_campus
Natural gas | therms/MMBtu | 0 | 0 | 0 | 0 | 0 | N/A | No gas heat | Htg_0_therm_per_MMBtu_campus
Water | CCF/MMBtu | 0.0035641 | 0.0035641 | 0.0035641 | 0.0035641 | 0.0035641 | N/A | See global inputs | Htg_0_CCF_per_MMBtu_campus
Cooling
Electricity | kW/ton | 0.838 | 0.838 | 0.838 | 0.838 | 0.838 | N/A | New chillers | Clg_0_kWh_per_ton_campus
Water | CCF/ton-hr | 0.0034724 | 0.0034724 | 0.0034724 | 0.0034724 | 0.0034724 | N/A | See global inputs | Clg_0_CCF_per_ton_campus
Process Steam
Electricity | kWh/lb | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | N/A | See global inputs | Process_0_kWh_per_lb_campus
Natural gas | therms/lb | 0 | 0 | 0 | 0 | 0 | N/A | No gas process steam | Process_0_therm_per_lb_campus
Water | CCF/lb | 0.00016863 | 0.00016863 | 0.00016863 | 0.00016863 | 0.00016863 | N/A |  | Process_0_CCF_per_lb_campus
Electricity
Electricity | kWh/kWh | 102% | 102% | 102% | 102% | 102% | N/A | New transformers have higher efficiency | Elec_0_kWh_per_kWh_campus
Enhancements
Electricity | kWh/y
Natural gas | therms/y
Water | CCF/y
Core Option 1C
Parameter | Unit | Value | [5 empty] | Source
Heating |  | Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Campus
Electricity | kWh/MMBh | 77.5134 | 77.5134 | 77.5134 | 77.5134 | 77.5134 | N/A | See global inputs |  | Htg_1C_kWh_per_MMBtu_libraries
Natural gas | therms/MMBtu | 0 | 0 | 0 | 0 | 0 | N/A | No gas heat |  | Htg_1C_therm_per_MMBtu_libraries
Water | CCF/MMBtu | 0.0035641 | 0.0035641 | 0.0035641 | 0.0035641 | 0.0035641 | N/A | See global inputs |  | Htg_1C_CCF_per_MMBtu_libraries
Cooling
Electricity | kW/ton | 0.838 | 0.838 | 0.838 | 0.838 | 0.838 | N/A | New chillers |  | Clg_1C_kWh_per_ton_libraries
Water | CCF/ton-hr | 0.0034724 | 0.0034724 | 0.0034724 | 0.0034724 | 0.0034724 | N/A | See global inputs |  | Clg_1C_CCF_per_ton_libraries
Process Steam
Electricity | kWh/lb | 0.315 | 0.315 | 0.315 | 0.315 | 0.315 | N/A | See global inputs |  | Process_1C_kWh_per_lb_libraries
Natural gas | therms/lb | 0 | 0 | 0 | 0 | 0 | N/A | No gas process steam |  | Process_1C_therm_per_lb_libraries
Water | CCF/lb | 0.00016863 | 0.00016863 | 0.00016863 | 0.00016863 | 0.00016863 | N/A |  |  | Process_1C_CCF_per_lb_libraries
Electricity
Electricity | kWh/kWh | 102% | 102% | 102% | 102% | 102% | N/A | New transformers have higher efficiency |  | Elec_1C_kWh_per_kWh_libraries
Enhancements
Electricity | kWh/y
Natural gas | therms/y
Water | CCF/y
Core Option 2
Parameter | Unit | Value | [5 empty] | Source
Heating |  | Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Campus
Electricity | kWh/MMBh | N/A | N/A | N/A | N/A | N/A | 0 | No electric heat
Natural gas | therms/MMBtu | N/A | N/A | N/A | N/A | N/A | 16.4474 | See global inputs
Water | CCF/MMBtu | N/A | N/A | N/A | N/A | N/A | 0.0036354 | See global inputs
Cooling
Electricity | kW/ton | N/A | N/A | N/A | N/A | N/A | 1.107 | Weighted average of existing and new electric chiller efficiencies (new used for replaced absorbers)
Water | CCF/ton-hr | N/A | N/A | N/A | N/A | N/A | 0.0052086
Process Steam
Electricity | kWh/lb | N/A | N/A | N/A | N/A | N/A | 0 | No electric process steam
Natural gas | therms/lb | N/A | N/A | N/A | N/A | N/A | 0.011873 | See global inputs
Water | CCF/lb | N/A | N/A | N/A | N/A | N/A | 0.00016863
Electricity
Electricity | kWh/kWh | N/A | N/A | N/A | N/A | N/A | 105% | See global inputs
Enhancements
Electricity | kWh/y
Natural gas | therms/y
Water | CCF/y
Core Option 6
Parameter | Unit | Value | [5 empty] | Source
Heating |  | Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Campus
Electricity | kWh/MMBh | N/A | N/A | N/A | N/A | N/A | 0 | No electric heat
Natural gas | therms/MMBtu | N/A | N/A | N/A | N/A | N/A | 11.7955 | See global inputs
Water | CCF/MMBtu | N/A | N/A | N/A | N/A | N/A | 0.0035641 | See global inputs
Cooling
Electricity | kW/ton | N/A | N/A | N/A | N/A | N/A | 1.107 | Weighted average of existing and new electric chiller efficiencies (new used for replaced absorbers)
Water | CCF/ton-hr | N/A | N/A | N/A | N/A | N/A | 0.0052086
Process Steam
Electricity | kWh/lb | N/A | N/A | N/A | N/A | N/A | 0.315 | See global inputs
Natural gas | therms/lb | N/A | N/A | N/A | N/A | N/A | 0 | No gas process steam- trying to be "ZNE ready"
Water | CCF/lb | N/A | N/A | N/A | N/A | N/A | 0.00016863
Electricity
Electricity | kWh/kWh | N/A | N/A | N/A | N/A | N/A | 102% | See global inputs
Enhancements
Electricity | kWh/y
Natural gas | therms/y
Water | CCF/y
Core Option 8A
Parameter | Unit | Value | [5 empty] | Source
Heating |  | Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Campus
Electricity | kWh/MMBh | N/A | N/A | N/A | N/A | N/A | 321.2628 | See global inputs
Natural gas | therms/MMBtu | N/A | N/A | N/A | N/A | N/A | 0 | No gas heat
Water | CCF/MMBtu | N/A | N/A | N/A | N/A | N/A | 0.0035641 | See global inputs
Cooling
Electricity | kW/ton | N/A | N/A | N/A | N/A | N/A | 1.107 | Weighted average of existing and new electric chiller efficiencies (new used for replaced absorbers)
Water | CCF/ton-hr | N/A | N/A | N/A | N/A | N/A | 0.0052086
Process Steam
Electricity | kWh/lb | N/A | N/A | N/A | N/A | N/A | 0.315 | See global inputs
Natural gas | therms/lb | N/A | N/A | N/A | N/A | N/A | 0 | No gas process steam
Water | CCF/lb | N/A | N/A | N/A | N/A | N/A | 0.00016863
Electricity
Electricity | kWh/kWh | N/A | N/A | N/A | N/A | N/A | 102% | New transformers have higher efficiency
Enhancements
Electricity | kWh/y
Natural gas | therms/y
Water | CCF/y
Core Option 8B
Parameter | Unit | Value | [5 empty] | Source
Heating |  | Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Campus
Electricity | kWh/MMBh | N/A | N/A | N/A | N/A | N/A | 108.5187 | See global inputs
Natural gas | therms/MMBtu | N/A | N/A | N/A | N/A | N/A | 0 | No gas heat
Water | CCF/MMBtu | N/A | N/A | N/A | N/A | N/A | 0.0035641 | See global inputs
Cooling
Electricity | kW/ton | N/A | N/A | N/A | N/A | N/A | 1.107 | Weighted average of existing and new electric chiller efficiencies (new used for replaced absorbers)
Water | CCF/ton-hr | N/A | N/A | N/A | N/A | N/A | 0.0052086
Process Steam
Electricity | kWh/lb | N/A | N/A | N/A | N/A | N/A | 0.315 | See global inputs
Natural gas | therms/lb | N/A | N/A | N/A | N/A | N/A | 0 | No gas process steam
Water | CCF/lb | N/A | N/A | N/A | N/A | N/A | 0.00016863
Electricity
Electricity | kWh/kWh | N/A | N/A | N/A | N/A | N/A | 102% | New transformers have higher efficiency
Enhancements
Electricity | kWh/y
Natural gas | therms/y
Water | CCF/y
Core Option 10A
Parameter | Unit | Value | [5 empty] | Source
Heating |  | Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Campus
Electricity | kWh/MMBh | N/A | N/A | N/A | N/A | N/A | 0 | No electric heat
Natural gas | therms/MMBtu | N/A | N/A | N/A | N/A | N/A | 15.7391 | See global inputs
Water | CCF/MMBtu | N/A | N/A | N/A | N/A | N/A | 0.0863 | Vanderweil study (2015), assume distribution water leakage decreases from 20% to 10%
Cooling
Electricity | kW/ton | N/A | N/A | N/A | N/A | N/A | 1.25 | Existing chillers
Natural gas | therms/ton-hr | N/A | N/A | N/A | N/A | N/A | 1.2071 | See global inputs
Water | CCF/ton-hr | N/A | N/A | N/A | N/A | N/A | 0.0052086
Process Steam
Electricity | kWh/lb | N/A | N/A | N/A | N/A | N/A | 0 | No electric process steam
Natural gas | therms/lb | N/A | N/A | N/A | N/A | N/A | 0.019963 | See global inputs
Water | CCF/lb | N/A | N/A | N/A | N/A | N/A | 0.00018736
Electricity
Electricity | kWh/kWh | N/A | N/A | N/A | N/A | N/A | 102% | See global inputs
Enhancements
Electricity | kWh/y
Natural gas | therms/y
Water | CCF/y
Core Option 11A
Parameter | Unit | Value | [5 empty] | Source
Heating |  | Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Campus
Electricity | kWh/MMBh | N/A | N/A | N/A | N/A | N/A | 0 | No electric heat | Htg_0_kWh_per_MMBtu_campus
Natural gas | therms/MMBtu | N/A | N/A | N/A | N/A | N/A | 8.4254 | See global inputs | Htg_0_therm_per_MMBtu_campus
Water | CCF/MMBtu | N/A | N/A | N/A | N/A | N/A | 0.0035641 | See global inputs | Htg_0_CCF_per_MMBtu_campus
Cooling
Electricity | kW/ton | N/A | N/A | N/A | N/A | N/A | 0.838 | New chillers | Clg_0_kWh_per_ton_campus
Water | CCF/ton-hr | N/A | N/A | N/A | N/A | N/A | 0.0034724 | See global inputs | Clg_0_CCF_per_ton_campus
Process Steam
Electricity | kWh/lb | N/A | N/A | N/A | N/A | N/A | 0 | No electric process steam | Process_0_kWh_per_lb_campus
Natural gas | therms/lb | N/A | N/A | N/A | N/A | N/A | 0.011873 | See global inputs | Process_0_therm_per_lb_campus
Water | CCF/lb | N/A | N/A | N/A | N/A | N/A | 0.00016863 |  | Process_0_CCF_per_lb_campus
Electricity
Electricity | kWh/kWh | N/A | N/A | N/A | N/A | N/A | 105% | See global inputs | Elec_0_kWh_per_kWh_campus
Enhancements
Electricity | kWh/y
Natural gas | therms/y
Water | CCF/y
Core Option 11B
Parameter | Unit | Value | [5 empty] | Source
Heating |  | Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Campus
Electricity | kWh/MMBh | N/A | N/A | N/A | N/A | N/A | 229.4734 | See global inputs | Htg_0_kWh_per_MMBtu_campus
Natural gas | therms/MMBtu | N/A | N/A | N/A | N/A | N/A | 0 | No gas heat | Htg_0_therm_per_MMBtu_campus
Water | CCF/MMBtu | N/A | N/A | N/A | N/A | N/A | 0.0035641 | See global inputs | Htg_0_CCF_per_MMBtu_campus
Cooling
Electricity | kW/ton | N/A | N/A | N/A | N/A | N/A | 0.838 | New chillers | Clg_0_kWh_per_ton_campus
Water | CCF/ton-hr | N/A | N/A | N/A | N/A | N/A | 0.0034724 | See global inputs | Clg_0_CCF_per_ton_campus
Process Steam
Electricity | kWh/lb | N/A | N/A | N/A | N/A | N/A | 0.315 | See global inputs | Process_0_kWh_per_lb_campus
Natural gas | therms/lb | N/A | N/A | N/A | N/A | N/A | 0 | No gas process steam | Process_0_therm_per_lb_campus
Water | CCF/lb | N/A | N/A | N/A | N/A | N/A | 0.00016863 |  | Process_0_CCF_per_lb_campus
Electricity
Electricity | kWh/kWh | N/A | N/A | N/A | N/A | N/A | 102% | New transformers have higher efficiency | Elec_0_kWh_per_kWh_campus
Enhancements
Electricity | kWh/y
Natural gas | therms/y
Water | CCF/y
Core Option 11C
Parameter | Unit | Value | [5 empty] | Source
Heating |  | Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Campus
Electricity | kWh/MMBh | N/A | N/A | N/A | N/A | N/A | 77.5134 | See global inputs
Natural gas | therms/MMBtu | N/A | N/A | N/A | N/A | N/A | 0 | No gas heat
Water | CCF/MMBtu | N/A | N/A | N/A | N/A | N/A | 0.0035641 | See global inputs
Cooling
Electricity | kW/ton | N/A | N/A | N/A | N/A | N/A | 0.838 | New chillers
Water | CCF/ton-hr | N/A | N/A | N/A | N/A | N/A | 0.0034724 | See global inputs
Process Steam
Electricity | kWh/lb | N/A | N/A | N/A | N/A | N/A | 0.315 | See global inputs
Natural gas | therms/lb | N/A | N/A | N/A | N/A | N/A | 0 | No gas process steam
Water | CCF/lb | N/A | N/A | N/A | N/A | N/A | 0.00016863
Electricity
Electricity | kWh/kWh | N/A | N/A | N/A | N/A | N/A | 102% | New transformers have higher efficiency
Enhancements
Electricity | kWh/y
Natural gas | therms/y
Water | CCF/y
Core Option 12
Parameter | Unit | Value | [5 empty] | Source
Heating |  | Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Campus
Electricity | kWh/MMBh | 77.5134 | 0 | 77.5134 | 0 | 0 | N/A | Same as 1c for biosciences & engineering, same as 0 for others |  | Htg_12_kWh_per_MMBtu_libraries
Natural gas | therms/MMBtu | 0 | 20.5801 | 0 | 20.5801 | 20.5801 | N/A | Same as 1c for biosciences & engineering, same as 0 for others |  | Htg_12_therm_per_MMBtu_libraries
Water | CCF/MMBtu | 0.0035641 | 0.0863 | 0.0035641 | 0.0863 | 0.0863 | N/A | Same as 1c for biosciences & engineering, same as 0 for others |  | Htg_12_CCF_per_MMBtu_libraries
Cooling
Electricity | kW/ton | 0.838 | 1.25 | 0.838 | 1.25 | 1.25 | N/A | Same as 1c for biosciences & engineering, same as 0 for others |  | Clg_12_kWh_per_ton_libraries
Natural gas | therms/ton-hr | N/A | 1.2071 | N/A | 1.2071 | 1.2071 |  |  |  | Clg_12_therm_per_ton_libraries
Water | CCF/ton-hr | 0.0034724 | 0.0052086 | 0.0034724 | 0.0052086 | 0.0052086 | N/A | Same as 1c for biosciences & engineering, same as 0 for others |  | Clg_12_CCF_per_ton_libraries
Process Steam
Electricity | kWh/lb | 0.315 | 0 | 0.315 | 0 | 0 | N/A | Same as 1c for biosciences & engineering, same as 0 for others |  | Process_12_kWh_per_lb_libraries
Natural gas | therms/lb | 0 | 0.019963 | 0 | 0.019963 | 0.019963 | N/A | Same as 1c for biosciences & engineering, same as 0 for others |  | Process_12_therm_per_lb_libraries
Water | CCF/lb | 0.00016863 | 0.00018736 | 0.00016863 | 0.00018736 | 0.00018736 | N/A | Same as 1c for biosciences & engineering, same as 0 for others |  | Process_12_CCF_per_lb_libraries
Electricity
Electricity | kWh/kWh | 102% | 105% | 102% | 105% | 105% | N/A | Same as 1c for biosciences & engineering, same as 0 for others |  | Elec_12_kWh_per_kWh_libraries
Enhancements
Electricity | kWh/y
Natural gas | therms/y
Water | CCF/y

## Phasing (hidden)
Client | UC Berkeley |  | Input
Project | Campus energy study update |  | Lookup
Job Number | 267147 |  | Calculation
Output
Check
Phasing
Core Option Only
Core Option | Year Implemented
| Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Total
0
1A
1B
1C
2
8A
8B
11A
11B
11C
Battery Storage
Core Option | Year Implemented
| Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Total
0
1A
1B
1C
2
8A
8B
11A
11B
11C
Thermal Storage
Core Option | Year Implemented
| Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Total
0
1A
1B
1C
2
8A
8B
11A
11B
11C
Solar Hot Water
Core Option | Year Implemented
| Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Total
0
1A
1B
1C
2
8A
8B
11A
11B
11C
Carbon Capture & Storage
Core Option | Year Implemented
| Biosciences | Business and Law | Engineering, Physics, and Chemistry | Libraries | Lower Sproul Offices | Total
0
1A
1B
1C
2
8A
8B
11A
11B
11C

## Enhancement Inputs
Client | UC Berkeley |  | Input
Project | Campus energy study update |  | Lookup
Job Number | 267147 |  | Calculation
Output
Check
Inputs - Enhancements
Solar Hot Water
Core Option | Node | Required Area (sqft) | Usable Annual Output (MMBtu/y)
0 | Campus | 0 | 0
1a | Biosciences | 0 | 0
| Business and Law | 0 | 0
| Engineering, Physics and Chemistry | 0 | 0
| Lower Sproul offices | 0 | 0
1b | Biosciences | 0 | 0
| Business and Law | 0 | 0
| Engineering, Physics and Chemistry | 0 | 0
| Lower Sproul offices | 0 | 0
1c | Biosciences | 88605 | 18541.8367
| Business and Law | 0 | 0
| Engineering, Physics and Chemistry | 67155 | 14053.1239
| Lower Sproul offices | 127512 | 26683.6712
2 | Campus | 0 | 0
6 | Campus | 0 | 0
8a | Campus | 0 | 0
8b | Campus | 510748 | 106881.1695
10a | Campus | 0 | 0
11a | Campus | 0 | 0
11b | Campus | 0 | 0
11c | Campus | 120176 | 25148.5105
12 | Biosciences | 0 | 0
| Business and Law | 0 | 0
| Engineering, Physics and Chemistry | 0 | 0
| Lower Sproul offices | 0 | 0
Solar PV
Core Option | Node | Required Area (sqft) | Usable Annual Output (kWh/y)
0 | Campus | 0 | 0
1a | Biosciences | 0 | 0
| Business and Law | 0 | 0
| Engineering, Physics and Chemistry | 0 | 0
| Lower Sproul offices | 0 | 0
1b | Biosciences | 0 | 0
| Business and Law | 0 | 0
| Engineering, Physics and Chemistry | 0 | 0
| Lower Sproul offices | 0 | 0
1c | Biosciences | 0 | 0
| Business and Law | 0 | 0
| Engineering, Physics and Chemistry | 0 | 0
| Lower Sproul offices | 0 | 0
2 | Campus | 0 | 0
6 | Campus | 0 | 0
8a | Campus | 0 | 0
8b | Campus | 530000 | 14119366
10a | Campus | 0 | 0
11a | Campus | 0 | 0
11b | Campus | 0 | 0
11c | Campus | 0 | 0
12 | Biosciences | 0 | 0
| Business and Law | 0 | 0
| Engineering, Physics and Chemistry | 0 | 0
| Lower Sproul offices | 0 | 0
Available Buildings
Building | Usable Roof Area (sqft) | Year Constructed | Node
Peoples Park | 75600 | 2023 | Lower Sproul offices
Davis Hall (N) | 26250 | 2025 | Engineering, Physics and Chemistry
Hesse/O'Brien (N) | 39375 | 2025 | Engineering, Physics and Chemistry
Oxford Tract | 183750 | 2025 | Biosciences
Tolman Hall (N) (Climate Science Building) | 51187.5 | 2025 | Biosciences
Cory Hall (N) | 35000 | 2028 | Engineering, Physics and Chemistry
Donner Laboratory (N) | 17500 | 2028 | Engineering, Physics and Chemistry
Lewis Hall Addition | 15750 | 2028 | Engineering, Physics and Chemistry
Evans Hall (N) | 28875 | 2030 | Engineering, Physics and Chemistry
Edwards Stadium / Goldman Field New Quad (N) | 262500 | 2040 | Lower Sproul offices
Lewis Hall (N) | 15312.5 | 2040 | Engineering, Physics and Chemistry
Sequencing
Usable Roof Area (sqft)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
All Options | Biosciences | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5 | 234937.5
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Engineering, Physics and Chemistry | 65625 | 65625 | 65625 | 133875 | 133875 | 162750 | 162750 | 162750 | 162750 | 162750 | 162750 | 162750 | 162750 | 162750 | 162750 | 178062.5 | 178062.5 | 178062.5 | 178062.5 | 178062.5 | 178062.5 | 178062.5 | 178062.5 | 178062.5 | 178062.5 | 178062.5 | 178062.5 | 178062.5 | 178062.5 | 178062.5 | 178062.5
| Lower Sproul offices | 75600 | 75600 | 75600 | 75600 | 75600 | 75600 | 75600 | 75600 | 75600 | 75600 | 75600 | 75600 | 75600 | 75600 | 75600 | 338100 | 338100 | 338100 | 338100 | 338100 | 338100 | 338100 | 338100 | 338100 | 338100 | 338100 | 338100 | 338100 | 338100 | 338100 | 338100
| Campus | 376162.5 | 376162.5 | 376162.5 | 444412.5 | 444412.5 | 473287.5 | 473287.5 | 473287.5 | 473287.5 | 473287.5 | 473287.5 | 473287.5 | 473287.5 | 473287.5 | 473287.5 | 751100 | 751100 | 751100 | 751100 | 751100 | 751100 | 751100 | 751100 | 751100 | 751100 | 751100 | 751100 | 751100 | 751100 | 751100 | 751100
SHW Output (MMBtu/y)
0 | Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1a | Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1b | Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1c | Biosciences | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367 | 18541.8367
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Engineering, Physics and Chemistry | 13732.95 | 13732.95 | 13732.95 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239 | 14053.1239
| Lower Sproul offices | 15820.3584 | 15820.3584 | 15820.3584 | 15820.3584 | 15820.3584 | 15820.3584 | 15820.3584 | 15820.3584 | 15820.3584 | 15820.3584 | 15820.3584 | 15820.3584 | 15820.3584 | 15820.3584 | 15820.3584 | 26683.6712 | 26683.6712 | 26683.6712 | 26683.6712 | 26683.6712 | 26683.6712 | 26683.6712 | 26683.6712 | 26683.6712 | 26683.6712 | 26683.6712 | 26683.6712 | 26683.6712 | 26683.6712 | 26683.6712 | 26683.6712
| Campus | 48095.1451 | 48095.1451 | 48095.1451 | 48415.319 | 48415.319 | 48415.319 | 48415.319 | 48415.319 | 48415.319 | 48415.319 | 48415.319 | 48415.319 | 48415.319 | 48415.319 | 48415.319 | 59278.6318 | 59278.6318 | 59278.6318 | 59278.6318 | 59278.6318 | 59278.6318 | 59278.6318 | 59278.6318 | 59278.6318 | 59278.6318 | 59278.6318 | 59278.6318 | 59278.6318 | 59278.6318 | 59278.6318 | 59278.6318
2 | Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8a | Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8b | Campus | 78717.2694 | 78717.2694 | 78717.2694 | 92999.5374 | 92999.5374 | 99042.0354 | 99042.0354 | 99042.0354 | 99042.0354 | 99042.0354 | 99042.0354 | 99042.0354 | 99042.0354 | 99042.0354 | 99042.0354 | 106881.1695 | 106881.1695 | 106881.1695 | 106881.1695 | 106881.1695 | 106881.1695 | 106881.1695 | 106881.1695 | 106881.1695 | 106881.1695 | 106881.1695 | 106881.1695 | 106881.1695 | 106881.1695 | 106881.1695 | 106881.1695
10a | Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11a | Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11b | Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11c | Campus | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105 | 25148.5105
12 | Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV Output (kWh/y)
0 | Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1a | Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1b | Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1c | Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8a | Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8b | Campus | 10021086.8169 | 10021086.8169 | 10021086.8169 | 11839288.1933 | 11839288.1933 | 12608527.2372 | 12608527.2372 | 12608527.2372 | 12608527.2372 | 12608527.2372 | 12608527.2372 | 12608527.2372 | 12608527.2372 | 12608527.2372 | 12608527.2372 | 14119366 | 14119366 | 14119366 | 14119366 | 14119366 | 14119366 | 14119366 | 14119366 | 14119366 | 14119366 | 14119366 | 14119366 | 14119366 | 14119366 | 14119366 | 14119366
10a | Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11a | Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11b | Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11c | Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Campus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on C69: Erica Levine: From electrical calculations tab. Assumes 4 stores, 70% of roof area usable

## Core Loads
Client | UC Berkeley |  |  | Input
Project | Campus energy study update |  |  | Lookup
Job Number | 267147 |  |  | Calculation
Output
Check
Loads - Core Options
Option 0
Other Electricity Use (kWh/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 15277743.9074 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 74467327.6438 | 74467327.6438 | 7302984.6975 | 7353817.5781 | 7353817.5781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 5531260.86 | 5531260.86 | 5531260.86 | 5531260.86 | 5531260.86 | 5911722.2975 | 5911722.2975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 95276332.4112 | 95769075.2487 | 28604732.3024 | 28655565.183 | 28655565.183 | 5911722.2975 | 5911722.2975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 41100367.7599 | 41100367.7599 | 41100367.7599 | 39612639.3208 | 39612639.3208 | 39763990.6635 | 39763990.6635 | 38704492.5612 | 38704492.5612 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15390568.91 | 15390568.91 | 15390568.91 | 15390568.91 | 15364645.04 | 15364645.04 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 67164342.9463 | 80295904.0867 | 80295904.0867 | 88236897.7765 | 88236897.7765 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 79425262.459 | 79425262.459 | 79425262.459 | 79425262.459 | 82311974.959 | 82311974.959 | 82311974.959 | 82311974.959 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | Load projections
Campus | 41100367.7599 | 41100367.7599 | 108264710.7062 | 119908543.4075 | 119908543.4075 | 143788073.2856 | 143788073.2856 | 140406366.3175 | 140406366.3175 | 140077445.6604 | 140077445.6604 | 139331989.8463 | 139331989.8463 | 139306065.9763 | 139306065.9763 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | Load projections
Other Steam Use (lbs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | Load projections
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 35030010.6667 | 35030010.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 46914399.0468 | 46914399.0468 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 91218518.5164 | 91218518.5164 | 91218518.5164 | 91218518.5164 | 91218518.5164 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 35030010.6667 | 33517716.3333 | 33517716.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 29833701.9696 | 29833701.9696 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | Load projections
Campus | 91218518.5164 | 91218518.5164 | 126248529.1831 | 124736234.8497 | 124736234.8497 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 131323249.0622 | 131323249.0622 | 130364547.9769 | 130364547.9769 | 134987648.2001 | 134987648.2001 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | Load projections
Heating Use (MMBtu/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 249408.4643 | 249408.4643 | 31507.7268 | 31507.7268 | 31507.7268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 362528.8157 | 362528.8157 | 144628.0782 | 144628.0782 | 144628.0782 | 15010.9983 | 15010.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 342242.651 | 342242.651 | 342242.651 | 305603.3021 | 305603.3021 | 301207.8085 | 301207.8085 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 87477.431 | 87477.431 | 87477.431 | 87477.431 | 87287.5176 | 87287.5176 | 86872.0132 | 86872.0132 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 217900.7374 | 239582.0429 | 239582.0429 | 264563.4401 | 264563.4401 | 241469.5248 | 241469.5248 | 241469.5248 | 241469.5248 | 228160.8903 | 228160.8903 | 225094.656 | 225094.656 | 231209.6995 | 231209.6995 | 231209.6995 | 231209.6995 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 13436.6921 | 13436.6921 | 13436.6921 | 13436.6921 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | Load projections
Campus | 342242.651 | 342242.651 | 560143.3885 | 545185.345 | 545185.345 | 663880.6017 | 663880.6017 | 646535.5382 | 646535.5382 | 635903.6161 | 635903.6161 | 621020.6754 | 621020.6754 | 617764.5277 | 617764.5277 | 661805.7485 | 661805.7485 | 660128.7475 | 660128.7475 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | Load projections
Cooling Use (ton-hrs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 3544817.3884 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 10424562.7296 | 10424562.7296 | 1967263.6829 | 2793463.3429 | 2793463.3429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 1207501.712 | 1207501.712 | 1207501.712 | 1207501.712 | 1207501.712 | 3455696.232 | 3455696.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 15176881.8299 | 18780101.4499 | 10322802.4032 | 11149002.0632 | 11149002.0632 | 3455696.232 | 3455696.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 8678140.1264 | 8678140.1264 | 8678140.1264 | 8237611.3694 | 8237611.3694 | 9012734.2894 | 9012734.2894 | 8552617.6962 | 8552617.6962 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7070995.9867 | 7070995.9867 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 8457299.0467 | 12134985.2667 | 12134985.2667 | 16003705.2676 | 16003705.2676 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15033617.2375 | 15033617.2375 | 14997195.0129 | 14997195.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | Load projections
Campus | 8678140.1264 | 8678140.1264 | 17135439.173 | 20372596.6361 | 20372596.6361 | 32250734.1654 | 32250734.1654 | 34490563.321 | 34490563.321 | 34966396.6093 | 34966396.6093 | 34691683.9768 | 34691683.9768 | 34644151.5222 | 34644151.5222 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | Load projections
Options 1A, 1B, 1C
Other Electricity Use (kWh/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 23615064.7863 | 23615064.7863 | 23615064.7863 | 22575379.2515 | 22575379.2515 | 11060280.1275 | 11060280.1275 | 10328151.51 | 10328151.51 | 10328151.51 | 10328151.51 | 10328151.51 | 10328151.51 | 10328151.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 15277743.9074 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15390568.91 | 4836531.9851 | 4836531.9851 | 4836531.9851 | 4836531.9851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 74467327.6438 | 74467327.6438 | 74467327.6438 | 87649721.6648 | 87649721.6648 | 58301867.0747 | 58301867.0747 | 52892559.7016 | 52892559.7016 | 52892559.7016 | 19978471.0419 | 19501820.0358 | 19501820.0358 | 19501820.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 5531260.86 | 5531260.86 | 5531260.86 | 5531260.86 | 5531260.86 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 118891397.1975 | 119384140.035 | 119384140.035 | 131526848.5212 | 131526848.5212 | 91061054.3453 | 91061054.3453 | 84919618.3547 | 84919618.3547 | 84523002.4191 | 41054876.8345 | 40410474.1684 | 40410474.1684 | 40410474.1684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 17485302.9735 | 17485302.9735 | 17485302.9735 | 17037260.0693 | 17037260.0693 | 28703710.536 | 28703710.536 | 28376341.0512 | 28376341.0512 | 28444036.3298 | 28444036.3298 | 28444036.3298 | 28444036.3298 | 28444036.3298 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10554036.9249 | 10554036.9249 | 10554036.9249 | 10528113.0549 | 15364645.04 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 29935030.7017 | 29935030.7017 | 27110406.9116 | 27110406.9116 | 27110406.9116 | 60024495.5713 | 59923442.4233 | 59923442.4233 | 59923442.4233 | 79425262.459 | 82311974.959 | 82311974.959 | 82311974.959 | 82311974.959 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5743970.6375 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | Load projections
Campus | 17485302.9735 | 17485302.9735 | 17485302.9735 | 17037260.0693 | 17037260.0693 | 58638741.2378 | 58638741.2378 | 55486747.9627 | 55486747.9627 | 55554443.2413 | 99022568.8259 | 98921515.6779 | 98921515.6779 | 98895591.8079 | 139306065.9763 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | Load projections
Other Steam Use (lbs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | Load projections
Biosciences | 73820430.1049 | 73820430.1049 | 73820430.1049 | 73820430.1049 | 73820430.1049 | 38571010.3333 | 38571010.3333 | 38571010.3333 | 38571010.3333 | 38571010.3333 | 38571010.3333 | 38571010.3333 | 38571010.3333 | 38571010.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 2652353.1429 | 2652353.1429 | 2652353.1429 | 2652353.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 35030010.6667 | 35030010.6667 | 35030010.6667 | 33517716.3333 | 33517716.3333 | 27281130.8333 | 27281130.8333 | 27281130.8333 | 27281130.8333 | 27281130.8333 | 27281130.8333 | 25435642.5711 | 25435642.5711 | 24476941.4858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 120734829.1517 | 120734829.1517 | 120734829.1517 | 119222534.8184 | 119222534.8184 | 77736529.5468 | 77736529.5468 | 77736529.5468 | 77736529.5468 | 77736529.5468 | 68504494.3095 | 66659006.0473 | 66659006.0473 | 65700304.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 17398088.4114 | 17398088.4114 | 17398088.4114 | 17398088.4114 | 17398088.4114 | 51034148.3791 | 51034148.3791 | 51034148.3791 | 51034148.3791 | 51034148.3791 | 51034148.3791 | 51034148.3791 | 51034148.3791 | 51034148.3791 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9232035.2373 | 9232035.2373 | 9232035.2373 | 9232035.2373 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 4717161.5 | 4717161.5 | 4717161.5 | 4717161.5 | 4717161.5 | 4717161.5 | 4398059.3985 | 4398059.3985 | 4398059.3985 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | Load projections
Campus | 17398088.4114 | 17398088.4114 | 17398088.4114 | 17398088.4114 | 17398088.4114 | 55751309.8791 | 55751309.8791 | 55751309.8791 | 55751309.8791 | 55751309.8791 | 64983345.1164 | 64664243.0149 | 64664243.0149 | 64664243.0149 | 130364547.9769 | 134987648.2001 | 134987648.2001 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | Load projections
Heating Use (MMBtu/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 275637.6793 | 275637.6793 | 275637.6793 | 246000.5626 | 246000.5626 | 123860.8289 | 123860.8289 | 117292.5139 | 117292.5139 | 117292.5139 | 117292.5139 | 117292.5139 | 117292.5139 | 117292.5139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 87477.431 | 27483.6157 | 27483.6157 | 27483.6157 | 27483.6157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 249408.4643 | 249408.4643 | 249408.4643 | 271089.7698 | 271089.7698 | 187952.9435 | 187952.9435 | 171672.215 | 171672.215 | 171672.215 | 113062.3157 | 104812.7624 | 104812.7624 | 102917.3175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 13436.6921 | 13436.6921 | 13436.6921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 638166.495 | 638166.495 | 638166.495 | 630210.6837 | 630210.6837 | 424934.1238 | 424934.1238 | 402085.0802 | 402085.0802 | 391453.1581 | 272849.4435 | 263025.5841 | 263025.5841 | 261130.1392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 66604.9717 | 66604.9717 | 66604.9717 | 59602.7395 | 59602.7395 | 177346.9796 | 177346.9796 | 174653.1482 | 174653.1482 | 174653.1482 | 174653.1482 | 174653.1482 | 174653.1482 | 174653.1482 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59993.8153 | 59993.8153 | 59993.8153 | 59803.9019 | 87287.5176 | 86872.0132 | 86872.0132 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 76610.4966 | 76610.4966 | 69797.3098 | 69797.3098 | 69797.3098 | 128407.2091 | 123348.1279 | 123348.1279 | 122177.3385 | 225094.656 | 231209.6995 | 231209.6995 | 231209.6995 | 231209.6995 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13436.6921 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | Load projections
Campus | 66604.9717 | 66604.9717 | 66604.9717 | 59602.7395 | 59602.7395 | 253957.4762 | 253957.4762 | 244450.458 | 244450.458 | 244450.458 | 363054.1725 | 357995.0913 | 357995.0913 | 356634.3886 | 617764.5277 | 661805.7485 | 661805.7485 | 660128.7475 | 660128.7475 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | Load projections
Cooling Use (ton-hrs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 5955361.6784 | 5955361.6784 | 5955361.6784 | 5650188.7174 | 5650188.7174 | 2894303.68 | 2894303.68 | 2562022.08 | 2562022.08 | 2562022.08 | 2562022.08 | 2562022.08 | 2562022.08 | 2562022.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 3544817.3884 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7082106.2167 | 3093628.5364 | 3093628.5364 | 3093628.5364 | 3093628.5364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 10424562.7296 | 10424562.7296 | 10424562.7296 | 14928448.6096 | 14928448.6096 | 10989101.5535 | 10989101.5535 | 10513209.2421 | 10513209.2421 | 10513209.2421 | 5578510.6349 | 5445696.5659 | 5445696.5659 | 5417057.1077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 1207501.712 | 1207501.712 | 1207501.712 | 1207501.712 | 1207501.712 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 21132243.5083 | 24735463.1283 | 24735463.1283 | 28934176.0474 | 28934176.0474 | 24573396.0738 | 24573396.0738 | 23765222.1624 | 23765222.1624 | 23613033.7707 | 14689857.4833 | 14496668.3287 | 14496668.3287 | 14468028.8705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 2722778.448 | 2722778.448 | 2722778.448 | 2587422.652 | 2587422.652 | 6118430.6094 | 6118430.6094 | 5990595.6162 | 5990595.6162 | 6618617.2962 | 6618617.2962 | 6618617.2962 | 6618617.2962 | 6618617.2962 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3988477.6802 | 3988477.6802 | 3988477.6802 | 3977367.4502 | 7070995.9867 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 5014603.7141 | 5014603.7141 | 4734745.5423 | 4734745.5423 | 4734745.5423 | 9669444.1495 | 9587920.6717 | 9587920.6717 | 9580137.9051 | 14997195.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3395321.1464 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | Load projections
Campus | 2722778.448 | 2722778.448 | 2722778.448 | 2587422.652 | 2587422.652 | 11133034.3236 | 11133034.3236 | 10725341.1586 | 10725341.1586 | 11353362.8386 | 20276539.126 | 20195015.6482 | 20195015.6482 | 20176122.6516 | 34644151.5222 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | Load projections
Option 2
Other Electricity Use (kWh/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 41100367.7599 | 41100367.7599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 15277743.9074 | 15770486.7449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 74467327.6438 | 74467327.6438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 5531260.86 | 5531260.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 136376700.171 | 136869443.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 41100367.7599 | 39612639.3208 | 39612639.3208 | 39763990.6635 | 39763990.6635 | 38704492.5612 | 38704492.5612 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | Load projections
Business and Law | 0 | 0 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15390568.91 | 15390568.91 | 15390568.91 | 15390568.91 | 15364645.04 | 15364645.04 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 74467327.6438 | 87649721.6648 | 87649721.6648 | 88236897.7765 | 88236897.7765 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 79425262.459 | 79425262.459 | 79425262.459 | 79425262.459 | 82311974.959 | 82311974.959 | 82311974.959 | 82311974.959 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 5531260.86 | 5531260.86 | 5531260.86 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | Load projections
Campus | 0 | 0 | 136869443.0085 | 148564108.5905 | 148564108.5905 | 149699795.5831 | 149699795.5831 | 140406366.3175 | 140406366.3175 | 140077445.6604 | 140077445.6604 | 139331989.8463 | 139331989.8463 | 139306065.9763 | 139306065.9763 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | Load projections
Other Steam Use (lbs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | Load projections
Biosciences | 91218518.5164 | 91218518.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 11884388.3801 | 11884388.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 35030010.6667 | 35030010.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 138132917.5632 | 138132917.5632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 91218518.5164 | 91218518.5164 | 91218518.5164 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | Load projections
Business and Law | 0 | 0 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 35030010.6667 | 33517716.3333 | 33517716.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 29833701.9696 | 29833701.9696 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | Load projections
Campus | 0 | 0 | 138132917.5632 | 136620623.2298 | 136620623.2298 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 131323249.0622 | 131323249.0622 | 130364547.9769 | 130364547.9769 | 134987648.2001 | 134987648.2001 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | Load projections
Heating Use (MMBtu/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 342242.651 | 342242.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 98109.3531 | 98109.3531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 249408.4643 | 249408.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 15010.9983 | 15010.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 704771.4667 | 704771.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 342242.651 | 305603.3021 | 305603.3021 | 301207.8085 | 301207.8085 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | Load projections
Business and Law | 0 | 0 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 87477.431 | 87477.431 | 87477.431 | 87477.431 | 87287.5176 | 87287.5176 | 86872.0132 | 86872.0132 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 249408.4643 | 271089.7698 | 271089.7698 | 264563.4401 | 264563.4401 | 241469.5248 | 241469.5248 | 241469.5248 | 241469.5248 | 228160.8903 | 228160.8903 | 225094.656 | 225094.656 | 231209.6995 | 231209.6995 | 231209.6995 | 231209.6995 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 13436.6921 | 13436.6921 | 13436.6921 | 13436.6921 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | Load projections
Campus | 0 | 0 | 704771.4667 | 689813.4233 | 689813.4233 | 678891.6 | 678891.6 | 646535.5382 | 646535.5382 | 635903.6161 | 635903.6161 | 621020.6754 | 621020.6754 | 617764.5277 | 617764.5277 | 661805.7485 | 661805.7485 | 660128.7475 | 660128.7475 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | Load projections
Cooling Use (ton-hrs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 8678140.1264 | 8678140.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 3544817.3884 | 7148037.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 10424562.7296 | 10424562.7296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 1207501.712 | 1207501.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 23855021.9563 | 27458241.5763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 8678140.1264 | 8237611.3694 | 8237611.3694 | 9012734.2894 | 9012734.2894 | 8552617.6962 | 8552617.6962 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | Load projections
Business and Law | 0 | 0 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7070995.9867 | 7070995.9867 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 10424562.7296 | 14928448.6096 | 14928448.6096 | 16003705.2676 | 16003705.2676 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15033617.2375 | 15033617.2375 | 14997195.0129 | 14997195.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 1207501.712 | 1207501.712 | 1207501.712 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | Load projections
Campus | 0 | 0 | 27458241.5763 | 31521598.6994 | 31521598.6994 | 35706430.3974 | 35706430.3974 | 34490563.321 | 34490563.321 | 34966396.6093 | 34966396.6093 | 34691683.9768 | 34691683.9768 | 34644151.5222 | 34644151.5222 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | Load projections
Option 6
Other Electricity Use (kWh/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 41100367.7599 | 41100367.7599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 15277743.9074 | 15770486.7449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 74467327.6438 | 74467327.6438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 5531260.86 | 5531260.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 136376700.171 | 136869443.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 41100367.7599 | 39612639.3208 | 39612639.3208 | 39763990.6635 | 39763990.6635 | 38704492.5612 | 38704492.5612 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | Load projections
Business and Law | 0 | 0 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15390568.91 | 15390568.91 | 15390568.91 | 15390568.91 | 15364645.04 | 15364645.04 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 74467327.6438 | 87649721.6648 | 87649721.6648 | 88236897.7765 | 88236897.7765 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 79425262.459 | 79425262.459 | 79425262.459 | 79425262.459 | 82311974.959 | 82311974.959 | 82311974.959 | 82311974.959 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 5531260.86 | 5531260.86 | 5531260.86 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | Load projections
Campus | 0 | 0 | 136869443.0085 | 148564108.5905 | 148564108.5905 | 149699795.5831 | 149699795.5831 | 140406366.3175 | 140406366.3175 | 140077445.6604 | 140077445.6604 | 139331989.8463 | 139331989.8463 | 139306065.9763 | 139306065.9763 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | Load projections
Other Steam Use (lbs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | Load projections
Biosciences | 91218518.5164 | 91218518.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 11884388.3801 | 11884388.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 35030010.6667 | 35030010.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 138132917.5632 | 138132917.5632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 91218518.5164 | 91218518.5164 | 91218518.5164 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | Load projections
Business and Law | 0 | 0 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 35030010.6667 | 33517716.3333 | 33517716.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 29833701.9696 | 29833701.9696 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | Load projections
Campus | 0 | 0 | 138132917.5632 | 136620623.2298 | 136620623.2298 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 131323249.0622 | 131323249.0622 | 130364547.9769 | 130364547.9769 | 134987648.2001 | 134987648.2001 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | Load projections
Heating Use (MMBtu/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 342242.651 | 342242.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 98109.3531 | 98109.3531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 249408.4643 | 249408.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 15010.9983 | 15010.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 704771.4667 | 704771.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 342242.651 | 305603.3021 | 305603.3021 | 301207.8085 | 301207.8085 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | Load projections
Business and Law | 0 | 0 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 87477.431 | 87477.431 | 87477.431 | 87477.431 | 87287.5176 | 87287.5176 | 86872.0132 | 86872.0132 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 249408.4643 | 271089.7698 | 271089.7698 | 264563.4401 | 264563.4401 | 241469.5248 | 241469.5248 | 241469.5248 | 241469.5248 | 228160.8903 | 228160.8903 | 225094.656 | 225094.656 | 231209.6995 | 231209.6995 | 231209.6995 | 231209.6995 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 13436.6921 | 13436.6921 | 13436.6921 | 13436.6921 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | Load projections
Campus | 0 | 0 | 704771.4667 | 689813.4233 | 689813.4233 | 678891.6 | 678891.6 | 646535.5382 | 646535.5382 | 635903.6161 | 635903.6161 | 621020.6754 | 621020.6754 | 617764.5277 | 617764.5277 | 661805.7485 | 661805.7485 | 660128.7475 | 660128.7475 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | Load projections
Cooling Use (ton-hrs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 8678140.1264 | 8678140.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 3544817.3884 | 7148037.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 10424562.7296 | 10424562.7296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 1207501.712 | 1207501.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 23855021.9563 | 27458241.5763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 8678140.1264 | 8237611.3694 | 8237611.3694 | 9012734.2894 | 9012734.2894 | 8552617.6962 | 8552617.6962 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | Load projections
Business and Law | 0 | 0 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7070995.9867 | 7070995.9867 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 10424562.7296 | 14928448.6096 | 14928448.6096 | 16003705.2676 | 16003705.2676 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15033617.2375 | 15033617.2375 | 14997195.0129 | 14997195.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 1207501.712 | 1207501.712 | 1207501.712 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | Load projections
Campus | 0 | 0 | 27458241.5763 | 31521598.6994 | 31521598.6994 | 35706430.3974 | 35706430.3974 | 34490563.321 | 34490563.321 | 34966396.6093 | 34966396.6093 | 34691683.9768 | 34691683.9768 | 34644151.5222 | 34644151.5222 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | Load projections
Options 8A, 8B
Other Electricity Use (kWh/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 41100367.7599 | 41100367.7599 | 41100367.7599 | 39612639.3208 | 39612639.3208 | 39763990.6635 | 39763990.6635 | 38704492.5612 | 38704492.5612 | 38772187.8398 | 27166188.666 | 27166188.666 | 27166188.666 | 27166188.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 15277743.9074 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15390568.91 | 15390568.91 | 15390568.91 | 15390568.91 | 15364645.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 74467327.6438 | 74467327.6438 | 74467327.6438 | 87649721.6648 | 87649721.6648 | 27903533.4618 | 27903533.4618 | 24270222.4648 | 24270222.4648 | 24270222.4648 | 6088282.3251 | 6088282.3251 | 6088282.3251 | 6088282.3251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 5531260.86 | 5531260.86 | 5531260.86 | 5531260.86 | 5531260.86 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 136376700.171 | 136869443.0085 | 136869443.0085 | 148564108.5905 | 148564108.5905 | 89366431.2684 | 89366431.2684 | 84673622.1691 | 84673622.1691 | 84344701.5121 | 54556762.1985 | 54389010.5385 | 54389010.5385 | 54363086.6685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11605999.1738 | 11605999.1738 | 11605999.1738 | 11605999.1738 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15364645.04 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 60333364.3147 | 60333364.3147 | 55732744.1483 | 55732744.1483 | 55732744.1483 | 73914684.2881 | 73336980.134 | 73336980.134 | 73336980.134 | 79425262.459 | 82311974.959 | 82311974.959 | 82311974.959 | 82311974.959 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5743970.6375 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | Load projections
Campus | 0 | 0 | 0 | 0 | 0 | 60333364.3147 | 60333364.3147 | 55732744.1483 | 55732744.1483 | 55732744.1483 | 85520683.4619 | 84942979.3077 | 84942979.3077 | 84942979.3077 | 139306065.9763 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | Load projections
Other Steam Use (lbs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | Load projections
Biosciences | 91218518.5164 | 91218518.5164 | 91218518.5164 | 91218518.5164 | 91218518.5164 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 54355738.9409 | 54355738.9409 | 54355738.9409 | 54355738.9409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 35030010.6667 | 35030010.6667 | 35030010.6667 | 33517716.3333 | 33517716.3333 | 27281130.8333 | 27281130.8333 | 27281130.8333 | 27281130.8333 | 27281130.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 138132917.5632 | 138132917.5632 | 138132917.5632 | 136620623.2298 | 136620623.2298 | 128770677.9259 | 128770677.9259 | 128770677.9259 | 128770677.9259 | 128770677.9259 | 66240127.321 | 66240127.321 | 66240127.321 | 66240127.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35249419.7716 | 35249419.7716 | 35249419.7716 | 35249419.7716 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 4717161.5 | 4717161.5 | 4717161.5 | 4717161.5 | 4717161.5 | 31998292.3333 | 29833701.9696 | 29833701.9696 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | Load projections
Campus | 0 | 0 | 0 | 0 | 0 | 4717161.5 | 4717161.5 | 4717161.5 | 4717161.5 | 4717161.5 | 67247712.1049 | 65083121.7412 | 65083121.7412 | 64124420.6559 | 130364547.9769 | 134987648.2001 | 134987648.2001 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | Load projections
Heating Use (MMBtu/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 342242.651 | 342242.651 | 342242.651 | 305603.3021 | 305603.3021 | 301207.8085 | 301207.8085 | 291945.662 | 291945.662 | 291945.662 | 171048.3804 | 171048.3804 | 171048.3804 | 171048.3804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 87477.431 | 87477.431 | 87477.431 | 87477.431 | 87287.5176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 249408.4643 | 249408.4643 | 249408.4643 | 271089.7698 | 271089.7698 | 143967.4868 | 143967.4868 | 128749.7385 | 128749.7385 | 128749.7385 | 25437.4086 | 23970.9587 | 23970.9587 | 23638.2454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 13436.6921 | 13436.6921 | 13436.6921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 704771.4667 | 704771.4667 | 704771.4667 | 689813.4233 | 689813.4233 | 558295.6467 | 558295.6467 | 533815.752 | 533815.752 | 523183.8298 | 298974.2183 | 295933.4622 | 295933.4622 | 295410.8356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120897.2816 | 120897.2816 | 120897.2816 | 120897.2816 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87287.5176 | 86872.0132 | 86872.0132 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 120595.9533 | 120595.9533 | 112719.7862 | 112719.7862 | 112719.7862 | 216032.1162 | 204189.9316 | 204189.9316 | 201456.4105 | 225094.656 | 231209.6995 | 231209.6995 | 231209.6995 | 231209.6995 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13436.6921 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | Load projections
Campus | 0 | 0 | 0 | 0 | 0 | 120595.9533 | 120595.9533 | 112719.7862 | 112719.7862 | 112719.7862 | 336929.3978 | 325087.2132 | 325087.2132 | 322353.6922 | 617764.5277 | 661805.7485 | 661805.7485 | 660128.7475 | 660128.7475 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | Load projections
Cooling Use (ton-hrs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 8678140.1264 | 8678140.1264 | 8678140.1264 | 8237611.3694 | 8237611.3694 | 9012734.2894 | 9012734.2894 | 8552617.6962 | 8552617.6962 | 9180639.3762 | 5064964.102 | 5064964.102 | 5064964.102 | 5064964.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 3544817.3884 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7070995.9867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 10424562.7296 | 10424562.7296 | 10424562.7296 | 14928448.6096 | 14928448.6096 | 6973484.3263 | 6973484.3263 | 6629207.9921 | 6629207.9921 | 6629207.9921 | 2965166.7972 | 2961275.414 | 2961275.414 | 2953492.6475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 1207501.712 | 1207501.712 | 1207501.712 | 1207501.712 | 1207501.712 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 23855021.9563 | 27458241.5763 | 27458241.5763 | 31521598.6994 | 31521598.6994 | 26676209.4561 | 26676209.4561 | 25871816.5287 | 25871816.5287 | 26347649.817 | 18567933.3479 | 18503666.879 | 18503666.879 | 18484773.8825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4115675.2742 | 4115675.2742 | 4115675.2742 | 4115675.2742 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7070995.9867 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 9030220.9413 | 9030220.9413 | 8618746.7923 | 8618746.7923 | 8618746.7923 | 12282787.9872 | 12072341.8236 | 12072341.8236 | 12043702.3654 | 14997195.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3395321.1464 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | Load projections
Campus | 0 | 0 | 0 | 0 | 0 | 9030220.9413 | 9030220.9413 | 8618746.7923 | 8618746.7923 | 8618746.7923 | 16398463.2614 | 16188017.0978 | 16188017.0978 | 16159377.6397 | 34644151.5222 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | Load projections
Option 10A
Other Electricity Use (kWh/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 41100367.7599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 15277743.9074 | 15770486.7449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 74467327.6438 | 74467327.6438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 5531260.86 | 5531260.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 136376700.171 | 95769075.2487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 41100367.7599 | 41100367.7599 | 39612639.3208 | 39612639.3208 | 39763990.6635 | 39763990.6635 | 38704492.5612 | 38704492.5612 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | Load projections
Business and Law | 0 | 0 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15390568.91 | 15390568.91 | 15390568.91 | 15390568.91 | 15364645.04 | 15364645.04 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 74467327.6438 | 87649721.6648 | 87649721.6648 | 88236897.7765 | 88236897.7765 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 79425262.459 | 79425262.459 | 79425262.459 | 79425262.459 | 82311974.959 | 82311974.959 | 82311974.959 | 82311974.959 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 5531260.86 | 5531260.86 | 5531260.86 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | Load projections
Campus | 0 | 41100367.7599 | 136869443.0085 | 148564108.5905 | 148564108.5905 | 149699795.5831 | 149699795.5831 | 140406366.3175 | 140406366.3175 | 140077445.6604 | 140077445.6604 | 139331989.8463 | 139331989.8463 | 139306065.9763 | 139306065.9763 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | Load projections
Other Steam Use (lbs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | Load projections
Biosciences | 91218518.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 11884388.3801 | 11884388.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 35030010.6667 | 35030010.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 138132917.5632 | 46914399.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 91218518.5164 | 91218518.5164 | 91218518.5164 | 91218518.5164 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | Load projections
Business and Law | 0 | 0 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 35030010.6667 | 33517716.3333 | 33517716.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 29833701.9696 | 29833701.9696 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | Load projections
Campus | 0 | 91218518.5164 | 138132917.5632 | 136620623.2298 | 136620623.2298 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 131323249.0622 | 131323249.0622 | 130364547.9769 | 130364547.9769 | 134987648.2001 | 134987648.2001 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | Load projections
Heating Use (MMBtu/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 342242.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 98109.3531 | 98109.3531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 249408.4643 | 249408.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 15010.9983 | 15010.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 704771.4667 | 362528.8157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 342242.651 | 342242.651 | 305603.3021 | 305603.3021 | 301207.8085 | 301207.8085 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | Load projections
Business and Law | 0 | 0 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 87477.431 | 87477.431 | 87477.431 | 87477.431 | 87287.5176 | 87287.5176 | 86872.0132 | 86872.0132 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 249408.4643 | 271089.7698 | 271089.7698 | 264563.4401 | 264563.4401 | 241469.5248 | 241469.5248 | 241469.5248 | 241469.5248 | 228160.8903 | 228160.8903 | 225094.656 | 225094.656 | 231209.6995 | 231209.6995 | 231209.6995 | 231209.6995 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 13436.6921 | 13436.6921 | 13436.6921 | 13436.6921 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | Load projections
Campus | 0 | 342242.651 | 704771.4667 | 689813.4233 | 689813.4233 | 678891.6 | 678891.6 | 646535.5382 | 646535.5382 | 635903.6161 | 635903.6161 | 621020.6754 | 621020.6754 | 617764.5277 | 617764.5277 | 661805.7485 | 661805.7485 | 660128.7475 | 660128.7475 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | Load projections
Cooling Use (ton-hrs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 8678140.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 3544817.3884 | 7148037.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 10424562.7296 | 10424562.7296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 1207501.712 | 1207501.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 23855021.9563 | 18780101.4499 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 8678140.1264 | 8678140.1264 | 8237611.3694 | 8237611.3694 | 9012734.2894 | 9012734.2894 | 8552617.6962 | 8552617.6962 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | Load projections
Business and Law | 0 | 0 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7070995.9867 | 7070995.9867 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 10424562.7296 | 14928448.6096 | 14928448.6096 | 16003705.2676 | 16003705.2676 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15033617.2375 | 15033617.2375 | 14997195.0129 | 14997195.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 1207501.712 | 1207501.712 | 1207501.712 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | Load projections
Campus | 0 | 8678140.1264 | 27458241.5763 | 31521598.6994 | 31521598.6994 | 35706430.3974 | 35706430.3974 | 34490563.321 | 34490563.321 | 34966396.6093 | 34966396.6093 | 34691683.9768 | 34691683.9768 | 34644151.5222 | 34644151.5222 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | Load projections
Options 11A, 11B, 11C
Other Electricity Use (kWh/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 41100367.7599 | 41100367.7599 | 41100367.7599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 15277743.9074 | 15770486.7449 | 15770486.7449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 74467327.6438 | 74467327.6438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 5531260.86 | 5531260.86 | 5531260.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 136376700.171 | 136869443.0085 | 62402115.3648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 39612639.3208 | 39612639.3208 | 39763990.6635 | 39763990.6635 | 38704492.5612 | 38704492.5612 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | Load projections
Business and Law | 0 | 0 | 0 | 15770486.7449 | 15770486.7449 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15390568.91 | 15390568.91 | 15390568.91 | 15390568.91 | 15364645.04 | 15364645.04 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 74467327.6438 | 87649721.6648 | 87649721.6648 | 88236897.7765 | 88236897.7765 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 79425262.459 | 79425262.459 | 79425262.459 | 79425262.459 | 82311974.959 | 82311974.959 | 82311974.959 | 82311974.959 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 5531260.86 | 5531260.86 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | Load projections
Campus | 0 | 0 | 74467327.6438 | 148564108.5905 | 148564108.5905 | 149699795.5831 | 149699795.5831 | 140406366.3175 | 140406366.3175 | 140077445.6604 | 140077445.6604 | 139331989.8463 | 139331989.8463 | 139306065.9763 | 139306065.9763 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | Load projections
Other Steam Use (lbs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | Load projections
Biosciences | 91218518.5164 | 91218518.5164 | 91218518.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 11884388.3801 | 11884388.3801 | 11884388.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 35030010.6667 | 35030010.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 138132917.5632 | 138132917.5632 | 103102906.8965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 91218518.5164 | 91218518.5164 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | Load projections
Business and Law | 0 | 0 | 0 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 35030010.6667 | 33517716.3333 | 33517716.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 29833701.9696 | 29833701.9696 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | Load projections
Campus | 0 | 0 | 35030010.6667 | 136620623.2298 | 136620623.2298 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 131323249.0622 | 131323249.0622 | 130364547.9769 | 130364547.9769 | 134987648.2001 | 134987648.2001 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | Load projections
Heating Use (MMBtu/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 342242.651 | 342242.651 | 342242.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 98109.3531 | 98109.3531 | 98109.3531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 249408.4643 | 249408.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 15010.9983 | 15010.9983 | 15010.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 704771.4667 | 704771.4667 | 455363.0024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 305603.3021 | 305603.3021 | 301207.8085 | 301207.8085 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | Load projections
Business and Law | 0 | 0 | 0 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 87477.431 | 87477.431 | 87477.431 | 87477.431 | 87287.5176 | 87287.5176 | 86872.0132 | 86872.0132 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 249408.4643 | 271089.7698 | 271089.7698 | 264563.4401 | 264563.4401 | 241469.5248 | 241469.5248 | 241469.5248 | 241469.5248 | 228160.8903 | 228160.8903 | 225094.656 | 225094.656 | 231209.6995 | 231209.6995 | 231209.6995 | 231209.6995 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 13436.6921 | 13436.6921 | 13436.6921 | 13436.6921 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | Load projections
Campus | 0 | 0 | 249408.4643 | 689813.4233 | 689813.4233 | 678891.6 | 678891.6 | 646535.5382 | 646535.5382 | 635903.6161 | 635903.6161 | 621020.6754 | 621020.6754 | 617764.5277 | 617764.5277 | 661805.7485 | 661805.7485 | 660128.7475 | 660128.7475 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | Load projections
Cooling Use (ton-hrs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 8678140.1264 | 8678140.1264 | 8678140.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 3544817.3884 | 7148037.0084 | 7148037.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 10424562.7296 | 10424562.7296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 1207501.712 | 1207501.712 | 1207501.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 23855021.9563 | 27458241.5763 | 17033678.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 8237611.3694 | 8237611.3694 | 9012734.2894 | 9012734.2894 | 8552617.6962 | 8552617.6962 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | Load projections
Business and Law | 0 | 0 | 0 | 7148037.0084 | 7148037.0084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7070995.9867 | 7070995.9867 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 10424562.7296 | 14928448.6096 | 14928448.6096 | 16003705.2676 | 16003705.2676 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15033617.2375 | 15033617.2375 | 14997195.0129 | 14997195.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 1207501.712 | 1207501.712 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | Load projections
Campus | 0 | 0 | 10424562.7296 | 31521598.6994 | 31521598.6994 | 35706430.3974 | 35706430.3974 | 34490563.321 | 34490563.321 | 34966396.6093 | 34966396.6093 | 34691683.9768 | 34691683.9768 | 34644151.5222 | 34644151.5222 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | Load projections
Option 12
Other Electricity Use (kWh/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 41100367.7599 | 41100367.7599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 15277743.9074 | 15770486.7449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 74467327.6438 | 74467327.6438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 5531260.86 | 5531260.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 136376700.171 | 136869443.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 41100367.7599 | 39612639.3208 | 39612639.3208 | 39763990.6635 | 39763990.6635 | 38704492.5612 | 38704492.5612 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | Load projections
Business and Law | 0 | 0 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15390568.91 | 15390568.91 | 15390568.91 | 15390568.91 | 15364645.04 | 15364645.04 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 74467327.6438 | 87649721.6648 | 87649721.6648 | 88236897.7765 | 88236897.7765 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 79425262.459 | 79425262.459 | 79425262.459 | 79425262.459 | 82311974.959 | 82311974.959 | 82311974.959 | 82311974.959 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 5531260.86 | 5531260.86 | 5531260.86 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | Load projections
Campus | 0 | 0 | 136869443.0085 | 148564108.5905 | 148564108.5905 | 149699795.5831 | 149699795.5831 | 140406366.3175 | 140406366.3175 | 140077445.6604 | 140077445.6604 | 139331989.8463 | 139331989.8463 | 139306065.9763 | 139306065.9763 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | Load projections
Other Steam Use (lbs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | Load projections
Biosciences | 91218518.5164 | 91218518.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 11884388.3801 | 11884388.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 35030010.6667 | 35030010.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 138132917.5632 | 138132917.5632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 91218518.5164 | 91218518.5164 | 91218518.5164 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | Load projections
Business and Law | 0 | 0 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 35030010.6667 | 33517716.3333 | 33517716.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 29833701.9696 | 29833701.9696 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | Load projections
Campus | 0 | 0 | 138132917.5632 | 136620623.2298 | 136620623.2298 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 131323249.0622 | 131323249.0622 | 130364547.9769 | 130364547.9769 | 134987648.2001 | 134987648.2001 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | Load projections
Heating Use (MMBtu/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 342242.651 | 342242.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 98109.3531 | 98109.3531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 249408.4643 | 249408.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 15010.9983 | 15010.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 704771.4667 | 704771.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 342242.651 | 305603.3021 | 305603.3021 | 301207.8085 | 301207.8085 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | Load projections
Business and Law | 0 | 0 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 87477.431 | 87477.431 | 87477.431 | 87477.431 | 87287.5176 | 87287.5176 | 86872.0132 | 86872.0132 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 249408.4643 | 271089.7698 | 271089.7698 | 264563.4401 | 264563.4401 | 241469.5248 | 241469.5248 | 241469.5248 | 241469.5248 | 228160.8903 | 228160.8903 | 225094.656 | 225094.656 | 231209.6995 | 231209.6995 | 231209.6995 | 231209.6995 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 13436.6921 | 13436.6921 | 13436.6921 | 13436.6921 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | Load projections
Campus | 0 | 0 | 704771.4667 | 689813.4233 | 689813.4233 | 678891.6 | 678891.6 | 646535.5382 | 646535.5382 | 635903.6161 | 635903.6161 | 621020.6754 | 621020.6754 | 617764.5277 | 617764.5277 | 661805.7485 | 661805.7485 | 660128.7475 | 660128.7475 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | Load projections
Cooling Use (ton-hrs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 8678140.1264 | 8678140.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 3544817.3884 | 7148037.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 10424562.7296 | 10424562.7296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 1207501.712 | 1207501.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 23855021.9563 | 27458241.5763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 8678140.1264 | 8237611.3694 | 8237611.3694 | 9012734.2894 | 9012734.2894 | 8552617.6962 | 8552617.6962 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | Load projections
Business and Law | 0 | 0 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7070995.9867 | 7070995.9867 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 10424562.7296 | 14928448.6096 | 14928448.6096 | 16003705.2676 | 16003705.2676 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15033617.2375 | 15033617.2375 | 14997195.0129 | 14997195.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 1207501.712 | 1207501.712 | 1207501.712 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | Load projections
Campus | 0 | 0 | 27458241.5763 | 31521598.6994 | 31521598.6994 | 35706430.3974 | 35706430.3974 | 34490563.321 | 34490563.321 | 34966396.6093 | 34966396.6093 | 34691683.9768 | 34691683.9768 | 34644151.5222 | 34644151.5222 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | Load projections

## Loads - enhancements (hidden)
Client | UC Berkeley |  |  | Input
Project | Campus energy study update |  |  | Lookup
Job Number | 267147 |  |  | Calculation
Output
Check
Loads - Core Options
Option 0
Other Electricity Use (kWh/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 15277743.9074 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 74467327.6438 | 74467327.6438 | 7302984.6975 | 7353817.5781 | 7353817.5781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 5531260.86 | 5531260.86 | 5531260.86 | 5531260.86 | 5531260.86 | 5911722.2975 | 5911722.2975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 95276332.4112 | 95769075.2487 | 28604732.3024 | 28655565.183 | 28655565.183 | 5911722.2975 | 5911722.2975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 41100367.7599 | 41100367.7599 | 41100367.7599 | 39612639.3208 | 39612639.3208 | 39763990.6635 | 39763990.6635 | 38704492.5612 | 38704492.5612 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15390568.91 | 15390568.91 | 15390568.91 | 15390568.91 | 15364645.04 | 15364645.04 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 67164342.9463 | 80295904.0867 | 80295904.0867 | 88236897.7765 | 88236897.7765 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 79425262.459 | 79425262.459 | 79425262.459 | 79425262.459 | 82311974.959 | 82311974.959 | 82311974.959 | 82311974.959 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | Load projections
Campus | 41100367.7599 | 41100367.7599 | 108264710.7062 | 119908543.4075 | 119908543.4075 | 143788073.2856 | 143788073.2856 | 140406366.3175 | 140406366.3175 | 140077445.6604 | 140077445.6604 | 139331989.8463 | 139331989.8463 | 139306065.9763 | 139306065.9763 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | Load projections
Other Steam Use (lbs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | Load projections
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 35030010.6667 | 35030010.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 46914399.0468 | 46914399.0468 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 91218518.5164 | 91218518.5164 | 91218518.5164 | 91218518.5164 | 91218518.5164 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 35030010.6667 | 33517716.3333 | 33517716.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 29833701.9696 | 29833701.9696 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | Load projections
Campus | 91218518.5164 | 91218518.5164 | 126248529.1831 | 124736234.8497 | 124736234.8497 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 131323249.0622 | 131323249.0622 | 130364547.9769 | 130364547.9769 | 134987648.2001 | 134987648.2001 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | Load projections
Heating Use (MMBtu/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 249408.4643 | 249408.4643 | 31507.7268 | 31507.7268 | 31507.7268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 362528.8157 | 362528.8157 | 144628.0782 | 144628.0782 | 144628.0782 | 15010.9983 | 15010.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 342242.651 | 342242.651 | 342242.651 | 305603.3021 | 305603.3021 | 301207.8085 | 301207.8085 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 87477.431 | 87477.431 | 87477.431 | 87477.431 | 87287.5176 | 87287.5176 | 86872.0132 | 86872.0132 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 217900.7374 | 239582.0429 | 239582.0429 | 264563.4401 | 264563.4401 | 241469.5248 | 241469.5248 | 241469.5248 | 241469.5248 | 228160.8903 | 228160.8903 | 225094.656 | 225094.656 | 231209.6995 | 231209.6995 | 231209.6995 | 231209.6995 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 13436.6921 | 13436.6921 | 13436.6921 | 13436.6921 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | Load projections
Campus | 342242.651 | 342242.651 | 560143.3885 | 545185.345 | 545185.345 | 663880.6017 | 663880.6017 | 646535.5382 | 646535.5382 | 635903.6161 | 635903.6161 | 621020.6754 | 621020.6754 | 617764.5277 | 617764.5277 | 661805.7485 | 661805.7485 | 660128.7475 | 660128.7475 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | Load projections
Cooling Use (ton-hrs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 3544817.3884 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 10424562.7296 | 10424562.7296 | 1967263.6829 | 2793463.3429 | 2793463.3429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 1207501.712 | 1207501.712 | 1207501.712 | 1207501.712 | 1207501.712 | 3455696.232 | 3455696.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 15176881.8299 | 18780101.4499 | 10322802.4032 | 11149002.0632 | 11149002.0632 | 3455696.232 | 3455696.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 8678140.1264 | 8678140.1264 | 8678140.1264 | 8237611.3694 | 8237611.3694 | 9012734.2894 | 9012734.2894 | 8552617.6962 | 8552617.6962 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7070995.9867 | 7070995.9867 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 8457299.0467 | 12134985.2667 | 12134985.2667 | 16003705.2676 | 16003705.2676 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15033617.2375 | 15033617.2375 | 14997195.0129 | 14997195.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | Load projections
Campus | 8678140.1264 | 8678140.1264 | 17135439.173 | 20372596.6361 | 20372596.6361 | 32250734.1654 | 32250734.1654 | 34490563.321 | 34490563.321 | 34966396.6093 | 34966396.6093 | 34691683.9768 | 34691683.9768 | 34644151.5222 | 34644151.5222 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | Load projections
Options 1A, 1B, 1C
Other Electricity Use (kWh/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 23615064.7863 | 23615064.7863 | 23615064.7863 | 22575379.2515 | 22575379.2515 | 11060280.1275 | 11060280.1275 | 10328151.51 | 10328151.51 | 10328151.51 | 10328151.51 | 10328151.51 | 10328151.51 | 10328151.51 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 15277743.9074 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15390568.91 | 4836531.9851 | 4836531.9851 | 4836531.9851 | 4836531.9851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 74467327.6438 | 74467327.6438 | 74467327.6438 | 87649721.6648 | 87649721.6648 | 58301867.0747 | 58301867.0747 | 52892559.7016 | 52892559.7016 | 52892559.7016 | 19978471.0419 | 19501820.0358 | 19501820.0358 | 19501820.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 5531260.86 | 5531260.86 | 5531260.86 | 5531260.86 | 5531260.86 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 118891397.1975 | 119384140.035 | 119384140.035 | 131526848.5212 | 131526848.5212 | 91061054.3453 | 91061054.3453 | 84919618.3547 | 84919618.3547 | 84523002.4191 | 41054876.8345 | 40410474.1684 | 40410474.1684 | 40410474.1684 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 17485302.9735 | 17485302.9735 | 17485302.9735 | 17037260.0693 | 17037260.0693 | 28703710.536 | 28703710.536 | 28376341.0512 | 28376341.0512 | 28444036.3298 | 28444036.3298 | 28444036.3298 | 28444036.3298 | 28444036.3298 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10554036.9249 | 10554036.9249 | 10554036.9249 | 10528113.0549 | 15364645.04 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 29935030.7017 | 29935030.7017 | 27110406.9116 | 27110406.9116 | 27110406.9116 | 60024495.5713 | 59923442.4233 | 59923442.4233 | 59923442.4233 | 79425262.459 | 82311974.959 | 82311974.959 | 82311974.959 | 82311974.959 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5743970.6375 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | Load projections
Campus | 17485302.9735 | 17485302.9735 | 17485302.9735 | 17037260.0693 | 17037260.0693 | 58638741.2378 | 58638741.2378 | 55486747.9627 | 55486747.9627 | 55554443.2413 | 99022568.8259 | 98921515.6779 | 98921515.6779 | 98895591.8079 | 139306065.9763 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | Load projections
Other Steam Use (lbs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | Load projections
Biosciences | 73820430.1049 | 73820430.1049 | 73820430.1049 | 73820430.1049 | 73820430.1049 | 38571010.3333 | 38571010.3333 | 38571010.3333 | 38571010.3333 | 38571010.3333 | 38571010.3333 | 38571010.3333 | 38571010.3333 | 38571010.3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 2652353.1429 | 2652353.1429 | 2652353.1429 | 2652353.1429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 35030010.6667 | 35030010.6667 | 35030010.6667 | 33517716.3333 | 33517716.3333 | 27281130.8333 | 27281130.8333 | 27281130.8333 | 27281130.8333 | 27281130.8333 | 27281130.8333 | 25435642.5711 | 25435642.5711 | 24476941.4858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 120734829.1517 | 120734829.1517 | 120734829.1517 | 119222534.8184 | 119222534.8184 | 77736529.5468 | 77736529.5468 | 77736529.5468 | 77736529.5468 | 77736529.5468 | 68504494.3095 | 66659006.0473 | 66659006.0473 | 65700304.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 17398088.4114 | 17398088.4114 | 17398088.4114 | 17398088.4114 | 17398088.4114 | 51034148.3791 | 51034148.3791 | 51034148.3791 | 51034148.3791 | 51034148.3791 | 51034148.3791 | 51034148.3791 | 51034148.3791 | 51034148.3791 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9232035.2373 | 9232035.2373 | 9232035.2373 | 9232035.2373 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 4717161.5 | 4717161.5 | 4717161.5 | 4717161.5 | 4717161.5 | 4717161.5 | 4398059.3985 | 4398059.3985 | 4398059.3985 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | Load projections
Campus | 17398088.4114 | 17398088.4114 | 17398088.4114 | 17398088.4114 | 17398088.4114 | 55751309.8791 | 55751309.8791 | 55751309.8791 | 55751309.8791 | 55751309.8791 | 64983345.1164 | 64664243.0149 | 64664243.0149 | 64664243.0149 | 130364547.9769 | 134987648.2001 | 134987648.2001 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | Load projections
Heating Use (MMBtu/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 275637.6793 | 275637.6793 | 275637.6793 | 246000.5626 | 246000.5626 | 123860.8289 | 123860.8289 | 117292.5139 | 117292.5139 | 117292.5139 | 117292.5139 | 117292.5139 | 117292.5139 | 117292.5139 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 87477.431 | 27483.6157 | 27483.6157 | 27483.6157 | 27483.6157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 249408.4643 | 249408.4643 | 249408.4643 | 271089.7698 | 271089.7698 | 187952.9435 | 187952.9435 | 171672.215 | 171672.215 | 171672.215 | 113062.3157 | 104812.7624 | 104812.7624 | 102917.3175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 13436.6921 | 13436.6921 | 13436.6921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 638166.495 | 638166.495 | 638166.495 | 630210.6837 | 630210.6837 | 424934.1238 | 424934.1238 | 402085.0802 | 402085.0802 | 391453.1581 | 272849.4435 | 263025.5841 | 263025.5841 | 261130.1392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 66604.9717 | 66604.9717 | 66604.9717 | 59602.7395 | 59602.7395 | 177346.9796 | 177346.9796 | 174653.1482 | 174653.1482 | 174653.1482 | 174653.1482 | 174653.1482 | 174653.1482 | 174653.1482 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59993.8153 | 59993.8153 | 59993.8153 | 59803.9019 | 87287.5176 | 86872.0132 | 86872.0132 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 76610.4966 | 76610.4966 | 69797.3098 | 69797.3098 | 69797.3098 | 128407.2091 | 123348.1279 | 123348.1279 | 122177.3385 | 225094.656 | 231209.6995 | 231209.6995 | 231209.6995 | 231209.6995 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13436.6921 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | Load projections
Campus | 66604.9717 | 66604.9717 | 66604.9717 | 59602.7395 | 59602.7395 | 253957.4762 | 253957.4762 | 244450.458 | 244450.458 | 244450.458 | 363054.1725 | 357995.0913 | 357995.0913 | 356634.3886 | 617764.5277 | 661805.7485 | 661805.7485 | 660128.7475 | 660128.7475 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | Load projections
Cooling Use (ton-hrs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 5955361.6784 | 5955361.6784 | 5955361.6784 | 5650188.7174 | 5650188.7174 | 2894303.68 | 2894303.68 | 2562022.08 | 2562022.08 | 2562022.08 | 2562022.08 | 2562022.08 | 2562022.08 | 2562022.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 3544817.3884 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7082106.2167 | 3093628.5364 | 3093628.5364 | 3093628.5364 | 3093628.5364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 10424562.7296 | 10424562.7296 | 10424562.7296 | 14928448.6096 | 14928448.6096 | 10989101.5535 | 10989101.5535 | 10513209.2421 | 10513209.2421 | 10513209.2421 | 5578510.6349 | 5445696.5659 | 5445696.5659 | 5417057.1077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 1207501.712 | 1207501.712 | 1207501.712 | 1207501.712 | 1207501.712 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 21132243.5083 | 24735463.1283 | 24735463.1283 | 28934176.0474 | 28934176.0474 | 24573396.0738 | 24573396.0738 | 23765222.1624 | 23765222.1624 | 23613033.7707 | 14689857.4833 | 14496668.3287 | 14496668.3287 | 14468028.8705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 2722778.448 | 2722778.448 | 2722778.448 | 2587422.652 | 2587422.652 | 6118430.6094 | 6118430.6094 | 5990595.6162 | 5990595.6162 | 6618617.2962 | 6618617.2962 | 6618617.2962 | 6618617.2962 | 6618617.2962 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3988477.6802 | 3988477.6802 | 3988477.6802 | 3977367.4502 | 7070995.9867 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 5014603.7141 | 5014603.7141 | 4734745.5423 | 4734745.5423 | 4734745.5423 | 9669444.1495 | 9587920.6717 | 9587920.6717 | 9580137.9051 | 14997195.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3395321.1464 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | Load projections
Campus | 2722778.448 | 2722778.448 | 2722778.448 | 2587422.652 | 2587422.652 | 11133034.3236 | 11133034.3236 | 10725341.1586 | 10725341.1586 | 11353362.8386 | 20276539.126 | 20195015.6482 | 20195015.6482 | 20176122.6516 | 34644151.5222 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | Load projections
Option 2
Other Electricity Use (kWh/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 41100367.7599 | 41100367.7599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 15277743.9074 | 15770486.7449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 74467327.6438 | 74467327.6438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 5531260.86 | 5531260.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 136376700.171 | 136869443.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 41100367.7599 | 39612639.3208 | 39612639.3208 | 39763990.6635 | 39763990.6635 | 38704492.5612 | 38704492.5612 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | Load projections
Business and Law | 0 | 0 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15390568.91 | 15390568.91 | 15390568.91 | 15390568.91 | 15364645.04 | 15364645.04 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 74467327.6438 | 87649721.6648 | 87649721.6648 | 88236897.7765 | 88236897.7765 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 79425262.459 | 79425262.459 | 79425262.459 | 79425262.459 | 82311974.959 | 82311974.959 | 82311974.959 | 82311974.959 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 5531260.86 | 5531260.86 | 5531260.86 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | Load projections
Campus | 0 | 0 | 136869443.0085 | 148564108.5905 | 148564108.5905 | 149699795.5831 | 149699795.5831 | 140406366.3175 | 140406366.3175 | 140077445.6604 | 140077445.6604 | 139331989.8463 | 139331989.8463 | 139306065.9763 | 139306065.9763 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | Load projections
Other Steam Use (lbs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | Load projections
Biosciences | 91218518.5164 | 91218518.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 11884388.3801 | 11884388.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 35030010.6667 | 35030010.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 138132917.5632 | 138132917.5632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 91218518.5164 | 91218518.5164 | 91218518.5164 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | Load projections
Business and Law | 0 | 0 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 35030010.6667 | 33517716.3333 | 33517716.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 29833701.9696 | 29833701.9696 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | Load projections
Campus | 0 | 0 | 138132917.5632 | 136620623.2298 | 136620623.2298 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 131323249.0622 | 131323249.0622 | 130364547.9769 | 130364547.9769 | 134987648.2001 | 134987648.2001 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | Load projections
Heating Use (MMBtu/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 342242.651 | 342242.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 98109.3531 | 98109.3531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 249408.4643 | 249408.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 15010.9983 | 15010.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 704771.4667 | 704771.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 342242.651 | 305603.3021 | 305603.3021 | 301207.8085 | 301207.8085 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | Load projections
Business and Law | 0 | 0 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 87477.431 | 87477.431 | 87477.431 | 87477.431 | 87287.5176 | 87287.5176 | 86872.0132 | 86872.0132 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 249408.4643 | 271089.7698 | 271089.7698 | 264563.4401 | 264563.4401 | 241469.5248 | 241469.5248 | 241469.5248 | 241469.5248 | 228160.8903 | 228160.8903 | 225094.656 | 225094.656 | 231209.6995 | 231209.6995 | 231209.6995 | 231209.6995 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 13436.6921 | 13436.6921 | 13436.6921 | 13436.6921 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | Load projections
Campus | 0 | 0 | 704771.4667 | 689813.4233 | 689813.4233 | 678891.6 | 678891.6 | 646535.5382 | 646535.5382 | 635903.6161 | 635903.6161 | 621020.6754 | 621020.6754 | 617764.5277 | 617764.5277 | 661805.7485 | 661805.7485 | 660128.7475 | 660128.7475 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | Load projections
Cooling Use (ton-hrs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 8678140.1264 | 8678140.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 3544817.3884 | 7148037.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 10424562.7296 | 10424562.7296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 1207501.712 | 1207501.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 23855021.9563 | 27458241.5763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 8678140.1264 | 8237611.3694 | 8237611.3694 | 9012734.2894 | 9012734.2894 | 8552617.6962 | 8552617.6962 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | Load projections
Business and Law | 0 | 0 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7070995.9867 | 7070995.9867 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 10424562.7296 | 14928448.6096 | 14928448.6096 | 16003705.2676 | 16003705.2676 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15033617.2375 | 15033617.2375 | 14997195.0129 | 14997195.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 1207501.712 | 1207501.712 | 1207501.712 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | Load projections
Campus | 0 | 0 | 27458241.5763 | 31521598.6994 | 31521598.6994 | 35706430.3974 | 35706430.3974 | 34490563.321 | 34490563.321 | 34966396.6093 | 34966396.6093 | 34691683.9768 | 34691683.9768 | 34644151.5222 | 34644151.5222 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | Load projections
Options 8A, 8B
Other Electricity Use (kWh/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 41100367.7599 | 41100367.7599 | 41100367.7599 | 39612639.3208 | 39612639.3208 | 39763990.6635 | 39763990.6635 | 38704492.5612 | 38704492.5612 | 38772187.8398 | 27166188.666 | 27166188.666 | 27166188.666 | 27166188.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 15277743.9074 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 15770486.7449 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15390568.91 | 15390568.91 | 15390568.91 | 15390568.91 | 15364645.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 74467327.6438 | 74467327.6438 | 74467327.6438 | 87649721.6648 | 87649721.6648 | 27903533.4618 | 27903533.4618 | 24270222.4648 | 24270222.4648 | 24270222.4648 | 6088282.3251 | 6088282.3251 | 6088282.3251 | 6088282.3251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 5531260.86 | 5531260.86 | 5531260.86 | 5531260.86 | 5531260.86 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 136376700.171 | 136869443.0085 | 136869443.0085 | 148564108.5905 | 148564108.5905 | 89366431.2684 | 89366431.2684 | 84673622.1691 | 84673622.1691 | 84344701.5121 | 54556762.1985 | 54389010.5385 | 54389010.5385 | 54363086.6685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11605999.1738 | 11605999.1738 | 11605999.1738 | 11605999.1738 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15364645.04 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 60333364.3147 | 60333364.3147 | 55732744.1483 | 55732744.1483 | 55732744.1483 | 73914684.2881 | 73336980.134 | 73336980.134 | 73336980.134 | 79425262.459 | 82311974.959 | 82311974.959 | 82311974.959 | 82311974.959 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5743970.6375 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | Load projections
Campus | 0 | 0 | 0 | 0 | 0 | 60333364.3147 | 60333364.3147 | 55732744.1483 | 55732744.1483 | 55732744.1483 | 85520683.4619 | 84942979.3077 | 84942979.3077 | 84942979.3077 | 139306065.9763 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | Load projections
Other Steam Use (lbs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | Load projections
Biosciences | 91218518.5164 | 91218518.5164 | 91218518.5164 | 91218518.5164 | 91218518.5164 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 54355738.9409 | 54355738.9409 | 54355738.9409 | 54355738.9409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 35030010.6667 | 35030010.6667 | 35030010.6667 | 33517716.3333 | 33517716.3333 | 27281130.8333 | 27281130.8333 | 27281130.8333 | 27281130.8333 | 27281130.8333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 138132917.5632 | 138132917.5632 | 138132917.5632 | 136620623.2298 | 136620623.2298 | 128770677.9259 | 128770677.9259 | 128770677.9259 | 128770677.9259 | 128770677.9259 | 66240127.321 | 66240127.321 | 66240127.321 | 66240127.321 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35249419.7716 | 35249419.7716 | 35249419.7716 | 35249419.7716 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 4717161.5 | 4717161.5 | 4717161.5 | 4717161.5 | 4717161.5 | 31998292.3333 | 29833701.9696 | 29833701.9696 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | Load projections
Campus | 0 | 0 | 0 | 0 | 0 | 4717161.5 | 4717161.5 | 4717161.5 | 4717161.5 | 4717161.5 | 67247712.1049 | 65083121.7412 | 65083121.7412 | 64124420.6559 | 130364547.9769 | 134987648.2001 | 134987648.2001 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | Load projections
Heating Use (MMBtu/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 342242.651 | 342242.651 | 342242.651 | 305603.3021 | 305603.3021 | 301207.8085 | 301207.8085 | 291945.662 | 291945.662 | 291945.662 | 171048.3804 | 171048.3804 | 171048.3804 | 171048.3804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 87477.431 | 87477.431 | 87477.431 | 87477.431 | 87287.5176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 249408.4643 | 249408.4643 | 249408.4643 | 271089.7698 | 271089.7698 | 143967.4868 | 143967.4868 | 128749.7385 | 128749.7385 | 128749.7385 | 25437.4086 | 23970.9587 | 23970.9587 | 23638.2454 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 13436.6921 | 13436.6921 | 13436.6921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 704771.4667 | 704771.4667 | 704771.4667 | 689813.4233 | 689813.4233 | 558295.6467 | 558295.6467 | 533815.752 | 533815.752 | 523183.8298 | 298974.2183 | 295933.4622 | 295933.4622 | 295410.8356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120897.2816 | 120897.2816 | 120897.2816 | 120897.2816 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87287.5176 | 86872.0132 | 86872.0132 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 120595.9533 | 120595.9533 | 112719.7862 | 112719.7862 | 112719.7862 | 216032.1162 | 204189.9316 | 204189.9316 | 201456.4105 | 225094.656 | 231209.6995 | 231209.6995 | 231209.6995 | 231209.6995 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13436.6921 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | Load projections
Campus | 0 | 0 | 0 | 0 | 0 | 120595.9533 | 120595.9533 | 112719.7862 | 112719.7862 | 112719.7862 | 336929.3978 | 325087.2132 | 325087.2132 | 322353.6922 | 617764.5277 | 661805.7485 | 661805.7485 | 660128.7475 | 660128.7475 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | Load projections
Cooling Use (ton-hrs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 8678140.1264 | 8678140.1264 | 8678140.1264 | 8237611.3694 | 8237611.3694 | 9012734.2894 | 9012734.2894 | 8552617.6962 | 8552617.6962 | 9180639.3762 | 5064964.102 | 5064964.102 | 5064964.102 | 5064964.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 3544817.3884 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 7148037.0084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7070995.9867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 10424562.7296 | 10424562.7296 | 10424562.7296 | 14928448.6096 | 14928448.6096 | 6973484.3263 | 6973484.3263 | 6629207.9921 | 6629207.9921 | 6629207.9921 | 2965166.7972 | 2961275.414 | 2961275.414 | 2953492.6475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 1207501.712 | 1207501.712 | 1207501.712 | 1207501.712 | 1207501.712 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 23855021.9563 | 27458241.5763 | 27458241.5763 | 31521598.6994 | 31521598.6994 | 26676209.4561 | 26676209.4561 | 25871816.5287 | 25871816.5287 | 26347649.817 | 18567933.3479 | 18503666.879 | 18503666.879 | 18484773.8825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4115675.2742 | 4115675.2742 | 4115675.2742 | 4115675.2742 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | Load projections
Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7070995.9867 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 9030220.9413 | 9030220.9413 | 8618746.7923 | 8618746.7923 | 8618746.7923 | 12282787.9872 | 12072341.8236 | 12072341.8236 | 12043702.3654 | 14997195.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3395321.1464 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | Load projections
Campus | 0 | 0 | 0 | 0 | 0 | 9030220.9413 | 9030220.9413 | 8618746.7923 | 8618746.7923 | 8618746.7923 | 16398463.2614 | 16188017.0978 | 16188017.0978 | 16159377.6397 | 34644151.5222 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | Load projections
Options 11A, 11B, 11C
Other Electricity Use (kWh/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 41100367.7599 | 41100367.7599 | 41100367.7599 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 15277743.9074 | 15770486.7449 | 15770486.7449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 74467327.6438 | 74467327.6438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 5531260.86 | 5531260.86 | 5531260.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 136376700.171 | 136869443.0085 | 62402115.3648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 39612639.3208 | 39612639.3208 | 39763990.6635 | 39763990.6635 | 38704492.5612 | 38704492.5612 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | 38772187.8398 | Load projections
Business and Law | 0 | 0 | 0 | 15770486.7449 | 15770486.7449 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15787184.8456 | 15390568.91 | 15390568.91 | 15390568.91 | 15390568.91 | 15364645.04 | 15364645.04 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 15384699.7344 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | 14843250.0175 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 74467327.6438 | 87649721.6648 | 87649721.6648 | 88236897.7765 | 88236897.7765 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 80002966.6132 | 79425262.459 | 79425262.459 | 79425262.459 | 79425262.459 | 82311974.959 | 82311974.959 | 82311974.959 | 82311974.959 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | 81863454.2387 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 5531260.86 | 5531260.86 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5911722.2975 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 5743970.6375 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | 36060627.4575 | Load projections
Campus | 0 | 0 | 74467327.6438 | 148564108.5905 | 148564108.5905 | 149699795.5831 | 149699795.5831 | 140406366.3175 | 140406366.3175 | 140077445.6604 | 140077445.6604 | 139331989.8463 | 139331989.8463 | 139306065.9763 | 139306065.9763 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172529489.9907 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 172080969.2703 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | 171539519.5534 | Load projections
Other Steam Use (lbs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | Load projections
Biosciences | 91218518.5164 | 91218518.5164 | 91218518.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 11884388.3801 | 11884388.3801 | 11884388.3801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 35030010.6667 | 35030010.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 138132917.5632 | 138132917.5632 | 103102906.8965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 91218518.5164 | 91218518.5164 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | 89605158.7125 | Load projections
Business and Law | 0 | 0 | 0 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11884388.3801 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | 11525540.602 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 35030010.6667 | 33517716.3333 | 33517716.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 31998292.3333 | 29833701.9696 | 29833701.9696 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | 28875000.8843 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | 4623100.2232 | Load projections
Campus | 0 | 0 | 35030010.6667 | 136620623.2298 | 136620623.2298 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 133487839.4259 | 131323249.0622 | 131323249.0622 | 130364547.9769 | 130364547.9769 | 134987648.2001 | 134987648.2001 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | 134628800.4219 | Load projections
Heating Use (MMBtu/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 342242.651 | 342242.651 | 342242.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 98109.3531 | 98109.3531 | 98109.3531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 249408.4643 | 249408.4643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 15010.9983 | 15010.9983 | 15010.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 704771.4667 | 704771.4667 | 455363.0024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 305603.3021 | 305603.3021 | 301207.8085 | 301207.8085 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | 291945.662 | Load projections
Business and Law | 0 | 0 | 0 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 98109.3531 | 87477.431 | 87477.431 | 87477.431 | 87477.431 | 87287.5176 | 87287.5176 | 86872.0132 | 86872.0132 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 85195.0121 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | 83077.0095 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 249408.4643 | 271089.7698 | 271089.7698 | 264563.4401 | 264563.4401 | 241469.5248 | 241469.5248 | 241469.5248 | 241469.5248 | 228160.8903 | 228160.8903 | 225094.656 | 225094.656 | 231209.6995 | 231209.6995 | 231209.6995 | 231209.6995 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | 229096.8228 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 15010.9983 | 13436.6921 | 13436.6921 | 13436.6921 | 13436.6921 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | 51778.3738 | Load projections
Campus | 0 | 0 | 249408.4643 | 689813.4233 | 689813.4233 | 678891.6 | 678891.6 | 646535.5382 | 646535.5382 | 635903.6161 | 635903.6161 | 621020.6754 | 621020.6754 | 617764.5277 | 617764.5277 | 661805.7485 | 661805.7485 | 660128.7475 | 660128.7475 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 658015.8708 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | 655897.8682 | Load projections
Cooling Use (ton-hrs/y)
Old System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 8678140.1264 | 8678140.1264 | 8678140.1264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Business and Law | 3544817.3884 | 7148037.0084 | 7148037.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Engineering, Physics and Chemistry | 10424562.7296 | 10424562.7296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 1207501.712 | 1207501.712 | 1207501.712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Campus | 23855021.9563 | 27458241.5763 | 17033678.8467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
New System | [30 empty] | Source
| 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Biosciences | 0 | 0 | 0 | 8237611.3694 | 8237611.3694 | 9012734.2894 | 9012734.2894 | 8552617.6962 | 8552617.6962 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | 9180639.3762 | Load projections
Business and Law | 0 | 0 | 0 | 7148037.0084 | 7148037.0084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7234294.6084 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7082106.2167 | 7070995.9867 | 7070995.9867 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7414629.3907 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | 7275034.2137 | Load projections
Engineering, Physics and Chemistry | 0 | 0 | 10424562.7296 | 14928448.6096 | 14928448.6096 | 16003705.2676 | 16003705.2676 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15247954.7844 | 15033617.2375 | 15033617.2375 | 14997195.0129 | 14997195.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15766985.0129 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | 15661982.6037 | Load projections
Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Load projections
Lower Sproul offices | 0 | 0 | 0 | 1207501.712 | 1207501.712 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3455696.232 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 3395321.1464 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | 8011631.8984 | Load projections
Campus | 0 | 0 | 10424562.7296 | 31521598.6994 | 31521598.6994 | 35706430.3974 | 35706430.3974 | 34490563.321 | 34490563.321 | 34966396.6093 | 34966396.6093 | 34691683.9768 | 34691683.9768 | 34644151.5222 | 34644151.5222 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40373885.6782 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40268883.269 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | 40129288.0921 | Load projections

## Core Commodities Use
Client | UC Berkeley |  | Input
Project | Campus energy study update |  | Lookup
Job Number | 267147 |  | Calculation
Output
Check
Commodity Use - Core Options
Option 0
Old System
Commodity | Unit | Year | [29 empty] | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Natural gas | therms/y | 18678271.7331 | 18678271.7331 | 11321364.5399 | 11321364.5399 | 11321364.5399 | 6358821.3213 | 6358821.3213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 152675.2986 | 171443.1225 | 81530.156 | 85833.5211 | 85833.5211 | 20590.3281 | 20590.3281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
New System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 0 | 0 | 0 | 0 | 16120936.062 | 16120936.062 | 15369930.1899 | 15369930.1899 | 15619355.1103 | 15619355.1103 | 14493235.7149 | 14493235.7149 | 14406600.0831 | 14406600.0831 | 56453362.9932 | 56453362.9932 | 56453362.9932 | 56453362.9932 | 55851163.2254 | 55851163.2254 | 55851163.2254 | 55851163.2254 | 55851163.2254 | 55851163.2254 | 55108147.0515 | 55108147.0515 | 55108147.0515 | 55108147.0515 | 55108147.0515 | Utility loads * efficiency inputs
Natural gas | therms/y | 13627747.2625 | 13627747.2625 | 18811462.7914 | 18473435.0882 | 18473435.0882 | 21090902.5224 | 21090902.5224 | 20733939.1692 | 20733939.1692 | 20515133.0185 | 20515133.0185 | 20165629.3435 | 20165629.3435 | 20079479.1879 | 20079479.1879 | 21078142.0574 | 21078142.0574 | 21036465.613 | 21036465.613 | 20992982.3742 | 20992982.3742 | 20992982.3742 | 20992982.3742 | 20992982.3742 | 20992982.3742 | 20949393.6433 | 20949393.6433 | 20949393.6433 | 20949393.6433 | 20949393.6433 | Utility loads * efficiency inputs
Water | CCF/y | 91827.643 | 91827.643 | 161246.6902 | 176533.6071 | 176533.6071 | 250285.5065 | 250285.5065 | 260455.0602 | 260455.0602 | 262015.963 | 262015.963 | 258895.1272 | 258895.1272 | 258186.9184 | 258186.9184 | 292697.9137 | 292697.9137 | 292485.954 | 292485.954 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 290846.8117 | 290846.8117 | 290846.8117 | 290846.8117 | 290846.8117 | Utility loads * efficiency inputs
Option 1A
Old System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Natural gas | therms/y | 28820560.6063 | 28820560.6063 | 28820560.6063 | 28545341.2881 | 28545341.2881 | 21374251.3975 | 21374251.3975 | 20706876.4783 | 20706876.4783 | 20396339.271 | 16670601.866 | 16331380.6211 | 16331380.6211 | 16248856.7698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 248660.2746 | 267428.0985 | 267428.0985 | 287568.1842 | 287568.1842 | 219650.4801 | 219650.4801 | 211497.2594 | 211497.2594 | 208869.4972 | 139746.1185 | 136609.5091 | 136609.5091 | 135907.3317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
New System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 20641256.4616 | 20641256.4616 | 20641256.4616 | 20057383.2552 | 20057383.2552 | 70900161.0628 | 70900161.0628 | 67248921.2517 | 67248921.2517 | 67846283.4621 | 120965437.0548 | 120791014.575 | 120791014.575 | 120747962.1804 | 175303168.2507 | 214989280.6885 | 214989280.6885 | 214989280.6885 | 214989280.6885 | 214430341.9133 | 214430341.9133 | 214430341.9133 | 214430341.9133 | 214430341.9133 | 214430341.9133 | 213744838.9523 | 213744838.9523 | 213744838.9523 | 213744838.9523 | 213744838.9523 | Sum of nodes
| Biosciences | 20641256.4616 | 20641256.4616 | 20641256.4616 | 20057383.2552 | 20057383.2552 | 35266140.9135 | 35266140.9135 | 34815277.2301 | 34815277.2301 | 35412639.4405 | 35412639.4405 | 35412639.4405 | 35412639.4405 | 35412639.4405 | 48404173.029 | 48404173.029 | 48404173.029 | 48404173.029 | 48404173.029 | 48404173.029 | 48404173.029 | 48404173.029 | 48404173.029 | 48404173.029 | 48404173.029 | 48404173.029 | 48404173.029 | 48404173.029 | 48404173.029 | 48404173.029 | Utility loads * efficiency inputs
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14424083.0672 | 14424083.0672 | 14424083.0672 | 14387552.6309 | 22058371.9288 | 22367394.1505 | 22367394.1505 | 22367394.1505 | 22367394.1505 | 22367394.1505 | 22367394.1505 | 22367394.1505 | 22367394.1505 | 22367394.1505 | 22367394.1505 | 21681891.1895 | 21681891.1895 | 21681891.1895 | 21681891.1895 | 21681891.1895 | Utility loads * efficiency inputs
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 35634020.1493 | 35634020.1493 | 32433644.0216 | 32433644.0216 | 32433644.0216 | 71128714.5471 | 70954292.0673 | 70954292.0673 | 70947770.109 | 95964175.0028 | 99640307.1478 | 99640307.1478 | 99640307.1478 | 99640307.1478 | 99081368.3726 | 99081368.3726 | 99081368.3726 | 99081368.3726 | 99081368.3726 | 99081368.3726 | 99081368.3726 | 99081368.3726 | 99081368.3726 | 99081368.3726 | 99081368.3726 | Utility loads * efficiency inputs
| Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8876448.29 | 44577406.3612 | 44577406.3612 | 44577406.3612 | 44577406.3612 | 44577406.3612 | 44577406.3612 | 44577406.3612 | 44577406.3612 | 44577406.3612 | 44577406.3612 | 44577406.3612 | 44577406.3612 | 44577406.3612 | 44577406.3612 | 44577406.3612 | Utility loads * efficiency inputs
Natural gas | therms/y | 767733.6633 | 767733.6633 | 767733.6633 | 708737.2918 | 708737.2918 | 2801603.6481 | 2801603.6481 | 2721503.5362 | 2721503.5362 | 2721503.5362 | 3830392.5211 | 3783979.3033 | 3783979.3033 | 3772514.8839 | 6752672.3299 | 7178624.458 | 7178624.458 | 7160234.6155 | 7160234.6155 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 7124587.9075 | Sum of nodes
| Biosciences | 767733.6633 | 767733.6633 | 767733.6633 | 708737.2918 | 708737.2918 | 2100126.6759 | 2100126.6759 | 2077430.1592 | 2077430.1592 | 2077430.1592 | 2077430.1592 | 2077430.1592 | 2077430.1592 | 2077430.1592 | 3523604.7947 | 3523604.7947 | 3523604.7947 | 3523604.7947 | 3523604.7947 | 3523604.7947 | 3523604.7947 | 3523604.7947 | 3523604.7947 | 3523604.7947 | 3523604.7947 | 3523604.7947 | 3523604.7947 | 3523604.7947 | 3523604.7947 | 3523604.7947 | Utility loads * efficiency inputs
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 615079.1077 | 615079.1077 | 615079.1077 | 613479.018 | 876529.1572 | 873028.3805 | 873028.3805 | 854638.538 | 854638.538 | 854638.538 | 854638.538 | 854638.538 | 854638.538 | 854638.538 | 854638.538 | 836793.5901 | 836793.5901 | 836793.5901 | 836793.5901 | 836793.5901 | Utility loads * efficiency inputs
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 701476.9722 | 701476.9722 | 644073.377 | 644073.377 | 644073.377 | 1137883.2542 | 1091470.0365 | 1091470.0365 | 1081605.7067 | 2239329.3235 | 2290850.8056 | 2290850.8056 | 2290850.8056 | 2290850.8056 | 2273049.0456 | 2273049.0456 | 2273049.0456 | 2273049.0456 | 2273049.0456 | 2273049.0456 | 2273049.0456 | 2273049.0456 | 2273049.0456 | 2273049.0456 | 2273049.0456 | Utility loads * efficiency inputs
| Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113209.0545 | 491140.4772 | 491140.4772 | 491140.4772 | 491140.4772 | 491140.4772 | 491140.4772 | 491140.4772 | 491140.4772 | 491140.4772 | 491140.4772 | 491140.4772 | 491140.4772 | 491140.4772 | 491140.4772 | 491140.4772 | Utility loads * efficiency inputs
Water | CCF/y | 12625.7826 | 12625.7826 | 12625.7826 | 12130.814 | 12130.814 | 48964.8007 | 48964.8007 | 47515.2358 | 47515.2358 | 49695.9893 | 82660.4609 | 82305.5373 | 82305.5373 | 82235.0832 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | Sum of nodes
| Biosciences | 12625.7826 | 12625.7826 | 12625.7826 | 12130.814 | 12130.814 | 30483.5186 | 30483.5186 | 30030.0211 | 30030.0211 | 32210.7745 | 32210.7745 | 32210.7745 | 32210.7745 | 32210.7745 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | Utility loads * efficiency inputs
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15620.2461 | 15620.2461 | 15620.2461 | 15580.9898 | 26868.5701 | 28060.3278 | 28060.3278 | 27993.8397 | 27993.8397 | 27993.8397 | 27993.8397 | 27993.8397 | 27993.8397 | 27993.8397 | 27993.8397 | 27501.5582 | 27501.5582 | 27501.5582 | 27501.5582 | 27501.5582 | Utility loads * efficiency inputs
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 18481.2821 | 18481.2821 | 17485.2148 | 17485.2148 | 17485.2148 | 34829.4403 | 34474.5167 | 34474.5167 | 34443.3189 | 57747.8622 | 60442.6891 | 60442.6891 | 60442.6891 | 60442.6891 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | Utility loads * efficiency inputs
| Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11837.8622 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | Utility loads * efficiency inputs
Option 1B
Old System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Natural gas | therms/y | 28820560.6063 | 28820560.6063 | 28820560.6063 | 28545341.2881 | 28545341.2881 | 21374251.3975 | 21374251.3975 | 20706876.4783 | 20706876.4783 | 20396339.271 | 16670601.866 | 16331380.6211 | 16331380.6211 | 16248856.7698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 248660.2746 | 267428.0985 | 267428.0985 | 287568.1842 | 287568.1842 | 219650.4801 | 219650.4801 | 211497.2594 | 211497.2594 | 208869.4972 | 139746.1185 | 136609.5091 | 136609.5091 | 135907.3317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
New System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 40881228.9773 | 40881228.9773 | 40881228.9773 | 38703970.8292 | 38703970.8292 | 144979354.6901 | 144979354.6901 | 139241066.597 | 139241066.597 | 139836397.949 | 221776033.222 | 220343199.3193 | 220343199.3193 | 219988679.5091 | 353949831.9547 | 402745531.6841 | 402745531.6841 | 402247666.1524 | 402247666.1524 | 401217333.9438 | 401217333.9438 | 401217333.9438 | 401217333.9438 | 401217333.9438 | 401217333.9438 | 400062049.1548 | 400062049.1548 | 400062049.1548 | 400062049.1548 | 400062049.1548 | Sum of nodes
| Biosciences | 40881228.9773 | 40881228.9773 | 40881228.9773 | 38703970.8292 | 38703970.8292 | 91177389.2194 | 91177389.2194 | 90118183.8858 | 90118183.8858 | 90713515.2378 | 90713515.2378 | 90713515.2378 | 90713515.2378 | 90713515.2378 | 142460726.4468 | 142460726.4468 | 142460726.4468 | 142460726.4468 | 142460726.4468 | 142460726.4468 | 142460726.4468 | 142460726.4468 | 142460726.4468 | 142460726.4468 | 142460726.4468 | 142460726.4468 | 142460726.4468 | 142460726.4468 | 142460726.4468 | 142460726.4468 | Utility loads * efficiency inputs
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30782572.7726 | 30782572.7726 | 30782572.7726 | 30703239.9822 | 45371223.6451 | 45584297.0102 | 45584297.0102 | 45086431.4785 | 45086431.4785 | 45086431.4785 | 45086431.4785 | 45086431.4785 | 45086431.4785 | 45086431.4785 | 45086431.4785 | 43931146.6895 | 43931146.6895 | 43931146.6895 | 43931146.6895 | 43931146.6895 | Utility loads * efficiency inputs
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 53801965.4707 | 53801965.4707 | 49122882.7112 | 49122882.7112 | 49122882.7112 | 100279945.2116 | 98847111.3089 | 98847111.3089 | 98571924.289 | 154330388.8618 | 159323159.6381 | 159323159.6381 | 159323159.6381 | 159323159.6381 | 158292827.4294 | 158292827.4294 | 158292827.4294 | 158292827.4294 | 158292827.4294 | 158292827.4294 | 158292827.4294 | 158292827.4294 | 158292827.4294 | 158292827.4294 | 158292827.4294 | Utility loads * efficiency inputs
| Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11787493.0011 | 55377348.5891 | 55377348.5891 | 55377348.5891 | 55377348.5891 | 55377348.5891 | 55377348.5891 | 55377348.5891 | 55377348.5891 | 55377348.5891 | 55377348.5891 | 55377348.5891 | 55377348.5891 | 55377348.5891 | 55377348.5891 | 55377348.5891 | Utility loads * efficiency inputs
Natural gas | therms/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Sum of nodes
| Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 12625.7826 | 12625.7826 | 12625.7826 | 12130.814 | 12130.814 | 48964.8007 | 48964.8007 | 47515.2358 | 47515.2358 | 49695.9893 | 82660.4609 | 82305.5373 | 82305.5373 | 82235.0832 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | Sum of nodes
| Biosciences | 12625.7826 | 12625.7826 | 12625.7826 | 12130.814 | 12130.814 | 30483.5186 | 30483.5186 | 30030.0211 | 30030.0211 | 32210.7745 | 32210.7745 | 32210.7745 | 32210.7745 | 32210.7745 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | Utility loads * efficiency inputs
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15620.2461 | 15620.2461 | 15620.2461 | 15580.9898 | 26868.5701 | 28060.3278 | 28060.3278 | 27993.8397 | 27993.8397 | 27993.8397 | 27993.8397 | 27993.8397 | 27993.8397 | 27993.8397 | 27993.8397 | 27501.5582 | 27501.5582 | 27501.5582 | 27501.5582 | 27501.5582 | Utility loads * efficiency inputs
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 18481.2821 | 18481.2821 | 17485.2148 | 17485.2148 | 17485.2148 | 34829.4403 | 34474.5167 | 34474.5167 | 34443.3189 | 57747.8622 | 60442.6891 | 60442.6891 | 60442.6891 | 60442.6891 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | Utility loads * efficiency inputs
| Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11837.8622 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | Utility loads * efficiency inputs
Option 1C
Old System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Natural gas | therms/y | 28820560.6063 | 28820560.6063 | 28820560.6063 | 28545341.2881 | 28545341.2881 | 21374251.3975 | 21374251.3975 | 20706876.4783 | 20706876.4783 | 20396339.271 | 16670601.866 | 16331380.6211 | 16331380.6211 | 16248856.7698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 248660.2746 | 267428.0985 | 267428.0985 | 287568.1842 | 287568.1842 | 219650.4801 | 219650.4801 | 211497.2594 | 211497.2594 | 208869.4972 | 139746.1185 | 136609.5091 | 136609.5091 | 135907.3317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
New System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 30759933.5382 | 30759933.5382 | 30759933.5382 | 29646735.0007 | 29646735.0007 | 106387961.5804 | 106387961.5804 | 102094360.5373 | 102094360.5373 | 102689691.8893 | 166606299.678 | 165942244.0495 | 165942244.0495 | 165794496.7125 | 260074297.7538 | 303633784.1218 | 303633784.1218 | 303390755.7758 | 303390755.7758 | 302681496.4296 | 302681496.4296 | 302681496.4296 | 302681496.4296 | 302681496.4296 | 302681496.4296 | 301848063.4395 | 301848063.4395 | 301848063.4395 | 301848063.4395 | 301848063.4395 | Sum of nodes
| Biosciences | 30759933.5382 | 30759933.5382 | 30759933.5382 | 29646735.0007 | 29646735.0007 | 64227731.7043 | 64227731.7043 | 63577881.1516 | 63577881.1516 | 64173212.5036 | 64173212.5036 | 64173212.5036 | 64173212.5036 | 64173212.5036 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | Utility loads * efficiency inputs
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21665909.0523 | 21665909.0523 | 21665909.0523 | 21615435.5074 | 32107007.3041 | 32383220.7396 | 32383220.7396 | 32140192.3936 | 32140192.3936 | 32140192.3936 | 32140192.3936 | 32140192.3936 | 32140192.3936 | 32140192.3936 | 32140192.3936 | 31306759.4035 | 31306759.4035 | 31306759.4035 | 31306759.4035 | 31306759.4035 | Utility loads * efficiency inputs
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 42160229.8761 | 42160229.8761 | 38516479.3857 | 38516479.3857 | 38516479.3857 | 80767178.122 | 80103122.4936 | 80103122.4936 | 80005848.7015 | 120124991.6156 | 124188520.0208 | 124188520.0208 | 124188520.0208 | 124188520.0208 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | Utility loads * efficiency inputs
| Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9745652.4724 | 48965396.9996 | 48965396.9996 | 48965396.9996 | 48965396.9996 | 48965396.9996 | 48965396.9996 | 48965396.9996 | 48965396.9996 | 48965396.9996 | 48965396.9996 | 48965396.9996 | 48965396.9996 | 48965396.9996 | 48965396.9996 | 48965396.9996 | Utility loads * efficiency inputs
Natural gas | therms/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Sum of nodes
| Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 12625.7826 | 12625.7826 | 12625.7826 | 12130.814 | 12130.814 | 48964.8007 | 48964.8007 | 47515.2358 | 47515.2358 | 49695.9893 | 82660.4609 | 82305.5373 | 82305.5373 | 82235.0832 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | Sum of nodes
| Biosciences | 12625.7826 | 12625.7826 | 12625.7826 | 12130.814 | 12130.814 | 30483.5186 | 30483.5186 | 30030.0211 | 30030.0211 | 32210.7745 | 32210.7745 | 32210.7745 | 32210.7745 | 32210.7745 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | Utility loads * efficiency inputs
| Business and Law | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15620.2461 | 15620.2461 | 15620.2461 | 15580.9898 | 26868.5701 | 28060.3278 | 28060.3278 | 27993.8397 | 27993.8397 | 27993.8397 | 27993.8397 | 27993.8397 | 27993.8397 | 27993.8397 | 27993.8397 | 27501.5582 | 27501.5582 | 27501.5582 | 27501.5582 | 27501.5582 | Utility loads * efficiency inputs
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 18481.2821 | 18481.2821 | 17485.2148 | 17485.2148 | 17485.2148 | 34829.4403 | 34474.5167 | 34474.5167 | 34443.3189 | 57747.8622 | 60442.6891 | 60442.6891 | 60442.6891 | 60442.6891 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | Utility loads * efficiency inputs
| Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Lower Sproul offices | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11837.8622 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | 28783.8494 | Utility loads * efficiency inputs
Option 2
Old System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 278436.8796 | 297204.7035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
New System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Natural gas | therms/y | 0 | 0 | 13231647.3488 | 12967671.8734 | 12967671.8734 | 12750842.004 | 12750842.004 | 12218669.9351 | 12218669.9351 | 12043802.7946 | 12043802.7946 | 11773318.0441 | 11773318.0441 | 11708380.6081 | 11708380.6081 | 12487631.4977 | 12487631.4977 | 12455788.7491 | 12455788.7491 | 12421037.4882 | 12421037.4882 | 12421037.4882 | 12421037.4882 | 12421037.4882 | 12421037.4882 | 12386201.9193 | 12386201.9193 | 12386201.9193 | 12386201.9193 | 12386201.9193 | Utility loads * efficiency inputs
Water | CCF/y | 0 | 0 | 168874.6507 | 189729.7682 | 189729.7682 | 210959.0178 | 210959.0178 | 204508.3938 | 204508.3938 | 206948.1803 | 206948.1803 | 205098.1932 | 205098.1932 | 204677.115 | 204677.115 | 235460.8406 | 235460.8406 | 235394.2329 | 235394.2329 | 234839.6335 | 234839.6335 | 234839.6335 | 234839.6335 | 234839.6335 | 234839.6335 | 234104.8346 | 234104.8346 | 234104.8346 | 234104.8346 | 234104.8346 | Utility loads * efficiency inputs
Option 6
Old System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 278436.8796 | 297204.7035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
New System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 0 | 213515470.0081 | 229465787.0952 | 229465787.0952 | 234269958.3774 | 234269958.3774 | 223444695.6728 | 223444695.6728 | 223635944.0528 | 223635944.0528 | 221889618.5061 | 221889618.5061 | 221508563.4493 | 221508563.4493 | 263195564.8147 | 263195564.8147 | 263082526.4769 | 263082526.4769 | 262508797.6753 | 262508797.6753 | 262508797.6753 | 262508797.6753 | 262508797.6753 | 262508797.6753 | 261801987.1032 | 261801987.1032 | 261801987.1032 | 261801987.1032 | 261801987.1032 | Utility loads * efficiency inputs
Natural gas | therms/y | 0 | 0 | 8313140.9881 | 8136703.1927 | 8136703.1927 | 8007874.6843 | 8007874.6843 | 7626218.3373 | 7626218.3373 | 7500809.3616 | 7500809.3616 | 7325257.4422 | 7325257.4422 | 7286849.5097 | 7286849.5097 | 7806338.3018 | 7806338.3018 | 7786557.2136 | 7786557.2136 | 7761634.7495 | 7761634.7495 | 7761634.7495 | 7761634.7495 | 7761634.7495 | 7761634.7495 | 7736651.8224 | 7736651.8224 | 7736651.8224 | 7736651.8224 | 7736651.8224 | Utility loads * efficiency inputs
Water | CCF/y | 0 | 0 | 168824.4131 | 189680.5968 | 189680.5968 | 210910.6249 | 210910.6249 | 204462.3073 | 204462.3073 | 206902.8517 | 206902.8517 | 205053.9254 | 205053.9254 | 204633.0794 | 204633.0794 | 235413.6656 | 235413.6656 | 235347.1775 | 235347.1775 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | Utility loads * efficiency inputs
Option 8A
Old System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 2865758.5346 | 20224353.7995 | 20224353.7995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 31258877.2831 | 30779136.7519 | 30779136.7519 | 26715362.4366 | 26715362.4366 | 26000353.613 | 26000353.613 | 25689816.4057 | 17369500.8413 | 17280686.4306 | 17280686.4306 | 17265421.5508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 278436.8796 | 297204.7035 | 297204.7035 | 315431.1862 | 315431.1862 | 265644.1021 | 265644.1021 | 257229.0903 | 257229.0903 | 257872.4582 | 163921.261 | 163061.6865 | 163061.6865 | 162873.0746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
New System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 0 | 0 | 0 | 0 | 111765402.8853 | 111765402.8853 | 104086948.9321 | 104086948.9321 | 104086948.9321 | 234810349.112 | 229501819.8474 | 229501819.8474 | 228289943.0458 | 419973326.8202 | 475809134.2023 | 475809134.2023 | 475157337.7931 | 475157337.7931 | 473904820.3144 | 473904820.3144 | 473904820.3144 | 473904820.3144 | 473904820.3144 | 473904820.3144 | 472517574.295 | 472517574.295 | 472517574.295 | 472517574.295 | 472517574.295 | Utility loads * efficiency inputs
Natural gas | therms/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 0 | 0 | 0 | 0 | 0 | 48260.2986 | 48260.2986 | 46089.0121 | 46089.0121 | 46089.0121 | 97954.0373 | 96450.6886 | 96450.6886 | 96130.1118 | 204633.0794 | 235413.6656 | 235413.6656 | 235347.1775 | 235347.1775 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | Utility loads * efficiency inputs
Option 8B
Old System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 2865758.5346 | 20224353.7995 | 20224353.7995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 31258877.2831 | 30779136.7519 | 30779136.7519 | 26715362.4366 | 26715362.4366 | 26000353.613 | 26000353.613 | 25689816.4057 | 17369500.8413 | 17280686.4306 | 17280686.4306 | 17265421.5508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 278436.8796 | 297204.7035 | 297204.7035 | 315431.1862 | 315431.1862 | 265644.1021 | 265644.1021 | 257229.0903 | 257229.0903 | 257872.4582 | 163921.261 | 163061.6865 | 163061.6865 | 162873.0746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
New System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 0 | 0 | 0 | 0 | 86109327.4072 | 86109327.4072 | 80106481.391 | 80106481.391 | 80106481.391 | 163130613.3908 | 160341438.8159 | 160341438.8159 | 159711102.4474 | 288547578.9388 | 335013877.191 | 335013877.191 | 334718852.8418 | 334718852.8418 | 333915837.3705 | 333915837.3705 | 333915837.3705 | 333915837.3705 | 333915837.3705 | 333915837.3705 | 332979183.8695 | 332979183.8695 | 332979183.8695 | 332979183.8695 | 332979183.8695 | Utility loads * efficiency inputs
Natural gas | therms/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 0 | 0 | 0 | 0 | 0 | 48260.2986 | 48260.2986 | 46089.0121 | 46089.0121 | 46089.0121 | 97954.0373 | 96450.6886 | 96450.6886 | 96130.1118 | 204633.0794 | 235413.6656 | 235413.6656 | 235347.1775 | 235347.1775 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | Utility loads * efficiency inputs
Option 10A
Old System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Natural gas | therms/y | 31258877.2831 | 18678271.7331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 278436.8796 | 171443.1225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
New System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 47837563.6783 | 168997147.2443 | 186004902.5418 | 186004902.5418 | 192394342.8968 | 192394342.8968 | 181395211.2003 | 181395211.2003 | 181654503.7405 | 181654503.7405 | 180550748.0195 | 180550748.0195 | 180464890.1038 | 180464890.1038 | 221514950.2935 | 221514950.2935 | 221514950.2935 | 221514950.2935 | 220926206.1473 | 220926206.1473 | 220926206.1473 | 220926206.1473 | 220926206.1473 | 220926206.1473 | 220199433.4649 | 220199433.4649 | 220199433.4649 | 220199433.4649 | 220199433.4649 | Utility loads * efficiency inputs
Natural gas | therms/y | 0 | 11970949.3343 | 18613368.2003 | 18347752.44 | 18347752.44 | 18113313.827 | 18113313.827 | 17604058.2587 | 17604058.2587 | 17436721.2821 | 17436721.2821 | 17159265.9771 | 17159265.9771 | 17088878.8445 | 17088878.8445 | 17874338.0026 | 17874338.0026 | 17840779.9266 | 17840779.9266 | 17807525.1315 | 17807525.1315 | 17807525.1315 | 17807525.1315 | 17807525.1315 | 17807525.1315 | 17774189.6589 | 17774189.6589 | 17774189.6589 | 17774189.6589 | 17774189.6589 | Utility loads * efficiency inputs
Water | CCF/y | 0 | 91827.643 | 229722.3986 | 249312.6806 | 249312.6806 | 269580.3854 | 269580.3854 | 260455.0602 | 260455.0602 | 262015.963 | 262015.963 | 258895.1272 | 258895.1272 | 258186.9184 | 258186.9184 | 292697.9137 | 292697.9137 | 292485.954 | 292485.954 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 290846.8117 | 290846.8117 | 290846.8117 | 290846.8117 | 290846.8117 | Utility loads * efficiency inputs
Option 11A
Old System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 22981692.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 278436.8796 | 297204.7035 | 191606.7622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
New System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 1011886.4347 | 1011886.4347 | 79202580.4606 | 155992314.02 | 155992314.02 | 157184785.3623 | 157184785.3623 | 147426684.6333 | 147426684.6333 | 147081317.9435 | 147081317.9435 | 146298589.3386 | 146298589.3386 | 146271369.2751 | 146271369.2751 | 181155964.4902 | 181155964.4902 | 181155964.4902 | 181155964.4902 | 180685017.7339 | 180685017.7339 | 180685017.7339 | 180685017.7339 | 180685017.7339 | 180685017.7339 | 180116495.5311 | 180116495.5311 | 180116495.5311 | 180116495.5311 | 180116495.5311 | Utility loads * efficiency inputs
Natural gas | therms/y | 0 | 0 | 2517258.683 | 7433987.211 | 7433987.211 | 7304772.2299 | 7304772.2299 | 7032160.5534 | 7032160.5534 | 6942582.7136 | 6942582.7136 | 6791488.9426 | 6791488.9426 | 6752672.3299 | 6752672.3299 | 7178624.458 | 7178624.458 | 7160234.6155 | 7160234.6155 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 7124587.9075 | Utility loads * efficiency inputs
Water | CCF/y | 0 | 0 | 42994.3265 | 134952.5224 | 134952.5224 | 148916.8093 | 148916.8093 | 144579.4907 | 144579.4907 | 146193.8892 | 146193.8892 | 144821.9214 | 144821.9214 | 144483.6016 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | Utility loads * efficiency inputs
Option 11B
Old System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 22981692.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 278436.8796 | 297204.7035 | 191606.7622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
New System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 1011886.4347 | 1011886.4347 | 145235755.5254 | 352865229.8041 | 352865229.8041 | 350530524.1432 | 350530524.1432 | 333626369.804 | 333626369.804 | 330851127.089 | 330851127.089 | 325993668.9907 | 325993668.9907 | 324918032.9792 | 324918032.9792 | 370368508.6459 | 370368508.6459 | 369870643.1142 | 369870643.1142 | 368928302.9244 | 368928302.9244 | 368928302.9244 | 368928302.9244 | 368928302.9244 | 368928302.9244 | 367889998.8936 | 367889998.8936 | 367889998.8936 | 367889998.8936 | 367889998.8936 | Utility loads * efficiency inputs
Natural gas | therms/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 0 | 0 | 42994.3265 | 134952.5224 | 134952.5224 | 148916.8093 | 148916.8093 | 144579.4907 | 144579.4907 | 146193.8892 | 146193.8892 | 144821.9214 | 144821.9214 | 144483.6016 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | Utility loads * efficiency inputs
Option 11C
Old System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 22981692.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 278436.8796 | 297204.7035 | 191606.7622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
New System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 1011886.4347 | 1011886.4347 | 107335630.5308 | 248041141.1728 | 248041141.1728 | 247366116.4245 | 247366116.4245 | 235378791.1501 | 235378791.1501 | 234219175.9536 | 234219175.9536 | 231623330.3926 | 231623330.3926 | 231042498.7782 | 231042498.7782 | 269800467.9235 | 269800467.9235 | 269557439.5775 | 269557439.5775 | 268936172.2502 | 268936172.2502 | 268936172.2502 | 268936172.2502 | 268936172.2502 | 268936172.2502 | 268219720.0183 | 268219720.0183 | 268219720.0183 | 268219720.0183 | 268219720.0183 | Utility loads * efficiency inputs
Natural gas | therms/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 0 | 0 | 42994.3265 | 134952.5224 | 134952.5224 | 148916.8093 | 148916.8093 | 144579.4907 | 144579.4907 | 146193.8892 | 146193.8892 | 144821.9214 | 144821.9214 | 144483.6016 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | Utility loads * efficiency inputs
Option 12
Old System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
Water | CCF/y | 278436.8796 | 297204.7035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
New System
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 0 | 226071828.5231 | 239769654.1745 | 239769654.1745 | 243575227.4488 | 243575227.4488 | 230569005.5643 | 230569005.5643 | 233025410.5537 | 233025410.5537 | 230656887.8044 | 230656887.8044 | 230089670.127 | 230089670.127 | 263403700.6801 | 263403700.6801 | 263792946.3144 | 263792946.3144 | 263083686.9682 | 263083686.9682 | 263083686.9682 | 263083686.9682 | 263083686.9682 | 263083686.9682 | 262832276.4728 | 262832276.4728 | 262832276.4728 | 262832276.4728 | 262832276.4728 | Sum of nodes
| Biosciences | 0 | 0 | 104457198.806 | 99730513.2514 | 99730513.2514 | 99685520.9764 | 99685520.9764 | 97501315.0097 | 97501315.0097 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | 98096646.3617 | Utility loads * efficiency inputs
| Business and Law | 0 | 0 | 2722076.1636 | 2722076.1636 | 2722076.1636 | 2847431.1694 | 2847431.1694 | 2847431.1694 | 2847431.1694 | 4708504.8068 | 4708504.8068 | 4708504.8068 | 4708504.8068 | 4711477.3958 | 4711477.3958 | 5258518.5364 | 5258518.5364 | 5647764.1707 | 5647764.1707 | 5647764.1707 | 5647764.1707 | 5647764.1707 | 5647764.1707 | 5647764.1707 | 5647764.1707 | 5396353.6753 | 5396353.6753 | 5396353.6753 | 5396353.6753 | 5396353.6753 | Utility loads * efficiency inputs
| Engineering, Physics and Chemistry | 0 | 0 | 115059527.6635 | 133484038.8696 | 133484038.8696 | 133999521.7537 | 133999521.7537 | 123177505.8359 | 123177505.8359 | 123177505.8359 | 123177505.8359 | 120695181.8821 | 120695181.8821 | 120124991.6156 | 120124991.6156 | 124188520.0208 | 124188520.0208 | 124188520.0208 | 124188520.0208 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | 123479260.6746 | Utility loads * efficiency inputs
| Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Lower Sproul offices | 0 | 0 | 3833025.89 | 3833025.89 | 3833025.89 | 7042753.5493 | 7042753.5493 | 7042753.5493 | 7042753.5493 | 7042753.5493 | 7042753.5493 | 7156554.7538 | 7156554.7538 | 7156554.7538 | 7156554.7538 | 35860015.7611 | 35860015.7611 | 35860015.7611 | 35860015.7611 | 35860015.7611 | 35860015.7611 | 35860015.7611 | 35860015.7611 | 35860015.7611 | 35860015.7611 | 35860015.7611 | 35860015.7611 | 35860015.7611 | 35860015.7611 | 35860015.7611 | Utility loads * efficiency inputs
Natural gas | therms/y | 0 | 0 | 2565274.1089 | 2565274.1089 | 2565274.1089 | 2565274.1089 | 2565274.1089 | 2565274.1089 | 2565274.1089 | 2346467.9582 | 2346467.9582 | 2314068.5606 | 2314068.5606 | 2310160.1223 | 2310160.1223 | 3182974.7107 | 3182974.7107 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3097709.5353 | 3097709.5353 | 3097709.5353 | 3097709.5353 | 3097709.5353 | Sum of nodes
| Biosciences | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Business and Law | 0 | 0 | 2256346.08 | 2256346.08 | 2256346.08 | 2256346.08 | 2256346.08 | 2256346.08 | 2256346.08 | 2037539.9293 | 2037539.9293 | 2037539.9293 | 2037539.9293 | 2033631.491 | 2033631.491 | 2025080.3642 | 2025080.3642 | 1983403.9198 | 1983403.9198 | 1983403.9198 | 1983403.9198 | 1983403.9198 | 1983403.9198 | 1983403.9198 | 1983403.9198 | 1939815.1889 | 1939815.1889 | 1939815.1889 | 1939815.1889 | 1939815.1889 | Utility loads * efficiency inputs
| Engineering, Physics and Chemistry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Lower Sproul offices | 0 | 0 | 308928.0289 | 308928.0289 | 308928.0289 | 308928.0289 | 308928.0289 | 308928.0289 | 308928.0289 | 308928.0289 | 308928.0289 | 276528.6313 | 276528.6313 | 276528.6313 | 276528.6313 | 1157894.3464 | 1157894.3464 | 1157894.3464 | 1157894.3464 | 1157894.3464 | 1157894.3464 | 1157894.3464 | 1157894.3464 | 1157894.3464 | 1157894.3464 | 1157894.3464 | 1157894.3464 | 1157894.3464 | 1157894.3464 | 1157894.3464 | Utility loads * efficiency inputs
Water | CCF/y | 0 | 0 | 145239.9156 | 159041.2633 | 159041.2633 | 177058.6462 | 177058.6462 | 172721.3277 | 172721.3277 | 173191.8538 | 173191.8538 | 171584.8106 | 171584.8106 | 171211.4885 | 171211.4885 | 203880.0341 | 203880.0341 | 203668.0744 | 203668.0744 | 203295.9317 | 203295.9317 | 203295.9317 | 203295.9317 | 203295.9317 | 203295.9317 | 202386.0489 | 202386.0489 | 202386.0489 | 202386.0489 | 202386.0489 | Sum of nodes
| Biosciences | 0 | 0 | 46735.7385 | 45075.4521 | 45075.4521 | 47479.2819 | 47479.2819 | 45848.5537 | 45848.5537 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | 48029.3071 | Utility loads * efficiency inputs
| Business and Law | 0 | 0 | 47924.9764 | 47924.9764 | 47924.9764 | 48374.26 | 48374.26 | 48374.26 | 48374.26 | 46664.0327 | 46664.0327 | 46664.0327 | 46664.0327 | 46589.7741 | 46589.7741 | 48343.774 | 48343.774 | 48131.8143 | 48131.8143 | 48131.8143 | 48131.8143 | 48131.8143 | 48131.8143 | 48131.8143 | 48131.8143 | 47221.9315 | 47221.9315 | 47221.9315 | 47221.9315 | 47221.9315 | Utility loads * efficiency inputs
| Engineering, Physics and Chemistry | 0 | 0 | 42994.3265 | 58455.9606 | 58455.9606 | 61910.2255 | 61910.2255 | 59203.6351 | 59203.6351 | 59203.6351 | 59203.6351 | 58046.9258 | 58046.9258 | 57747.8622 | 57747.8622 | 60442.6891 | 60442.6891 | 60442.6891 | 60442.6891 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | 60070.5464 | Utility loads * efficiency inputs
| Libraries | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Utility loads * efficiency inputs
| Lower Sproul offices | 0 | 0 | 7584.8741 | 7584.8741 | 7584.8741 | 19294.8789 | 19294.8789 | 19294.8789 | 19294.8789 | 19294.8789 | 19294.8789 | 18844.545 | 18844.545 | 18844.545 | 18844.545 | 47064.2639 | 47064.2639 | 47064.2639 | 47064.2639 | 47064.2639 | 47064.2639 | 47064.2639 | 47064.2639 | 47064.2639 | 47064.2639 | 47064.2639 | 47064.2639 | 47064.2639 | 47064.2639 | 47064.2639 | Utility loads * efficiency inputs

## Commodity use- enhancement (hidden)
Client | UC Berkeley |  | Input
Project | Campus energy study update |  | Lookup
Job Number | 267147 |  | Calculation
Output
Check
Enhancement Commodity Use
Option 0
Total
Commodity | Unit | Year | [30 empty] | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Option 1A
Biosciences
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Business and Law
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Engineering, Physics, and Chemistry
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Libraries
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Lower Sproul Offices
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Total
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sum of above
Natural gas | therms/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sum of above
Water | CCF/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sum of above
Option 1B
Biosciences
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Business and Law
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Engineering, Physics, and Chemistry
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Libraries
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Lower Sproul Offices
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Total
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sum of above
Natural gas | therms/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sum of above
Water | CCF/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sum of above
Option 1C
Biosciences
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Business and Law
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Engineering, Physics, and Chemistry
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Libraries
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Lower Sproul Offices
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Total
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | sum of above
Natural gas | therms/y | [31 empty] | sum of above
Water | CCF/y | [31 empty] | sum of above
Option 2
Total
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Option 8A
Biosciences
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Business and Law
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Engineering, Physics, and Chemistry
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Libraries
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Lower Sproul Offices
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Total
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sum of above
Natural gas | therms/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sum of above
Water | CCF/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sum of above
Option 8B
Biosciences
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Business and Law
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Engineering, Physics, and Chemistry
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Libraries
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Lower Sproul Offices
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Total
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sum of above
Natural gas | therms/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sum of above
Water | CCF/y | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | sum of above
Option 11A
Total
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Option 11B
Total
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs
Option 11C
Total
Commodity | Unit | Year 2025: Year | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Electricity | kWh/y | [31 empty] | Utility loads * efficiency inputs
Natural gas | therms/y | [31 empty] | Utility loads * efficiency inputs
Water | CCF/y | [31 empty] | Utility loads * efficiency inputs

## Outputs
Client | UC Berkeley |  | Input
Project | Campus energy study update |  | Lookup
Job Number | 267147 |  | Calculation
Output
Check
Outputs for LCCA
Core Options | [33 empty] | Graphs: All Options
Option 0 | [33 empty] | Electricity Use
Item | Unit | Year | [29 empty] | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 0 | 0 | 0 | 0 | 16120936.062 | 16120936.062 | 15369930.1899 | 15369930.1899 | 15619355.1103 | 15619355.1103 | 14493235.7149 | 14493235.7149 | 14406600.0831 | 14406600.0831 | 56453362.9932 | 56453362.9932 | 56453362.9932 | 56453362.9932 | 55851163.2254 | 55851163.2254 | 55851163.2254 | 55851163.2254 | 55851163.2254 | 55851163.2254 | 55108147.0515 | 55108147.0515 | 55108147.0515 | 55108147.0515 | 55108147.0515 | 988481280.9034 | Core commodity use tab
Natural gas | therms/y | 32306018.9957 | 32306018.9957 | 30132827.3313 | 29794799.6281 | 29794799.6281 | 27449723.8437 | 27449723.8437 | 20733939.1692 | 20733939.1692 | 20515133.0185 | 20515133.0185 | 20165629.3435 | 20165629.3435 | 20079479.1879 | 20079479.1879 | 21078142.0574 | 21078142.0574 | 21036465.613 | 21036465.613 | 20992982.3742 | 20992982.3742 | 20992982.3742 | 20992982.3742 | 20992982.3742 | 20992982.3742 | 20949393.6433 | 20949393.6433 | 20949393.6433 | 20949393.6433 | 20949393.6433 | 687156351.5073 | Core commodity use tab
Water | CCF/y | 244502.9416 | 263270.7656 | 242776.8462 | 262367.1282 | 262367.1282 | 270875.8345 | 270875.8345 | 260455.0602 | 260455.0602 | 262015.963 | 262015.963 | 258895.1272 | 258895.1272 | 258186.9184 | 258186.9184 | 292697.9137 | 292697.9137 | 292485.954 | 292485.954 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 290846.8117 | 290846.8117 | 290846.8117 | 290846.8117 | 290846.8117 | 8271284.5766 | Core commodity use tab
Carbon | tons CO2-eq/y | 217193.3657 | 217193.3657 | 202582.9981 | 200310.4379 | 200310.4379 | 184544.4934 | 184544.4934 | 139394.273 | 139394.273 | 137923.2393 | 137923.2393 | 135573.5261 | 135573.5261 | 134994.3386 | 134994.3386 | 141708.3491 | 141708.3491 | 141428.1583 | 141428.1583 | 141135.8205 | 141135.8205 | 141135.8205 | 141135.8205 | 141135.8205 | 141135.8205 | 140842.7735 | 140842.7735 | 140842.7735 | 140842.7735 | 140842.7735 | 4619752.1512
Energy | (MMBtu/y) | Year 2054: 2282968.3621 | 72088333.2812
Option 1A
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 20641256.4616 | 20641256.4616 | 20641256.4616 | 20057383.2552 | 20057383.2552 | 70900161.0628 | 70900161.0628 | 67248921.2517 | 67248921.2517 | 67846283.4621 | 120965437.0548 | 120791014.575 | 120791014.575 | 120747962.1804 | 175303168.2507 | 214989280.6885 | 214989280.6885 | 214989280.6885 | 214989280.6885 | 214430341.9133 | 214430341.9133 | 214430341.9133 | 214430341.9133 | 214430341.9133 | 214430341.9133 | 213744838.9523 | 213744838.9523 | 213744838.9523 | 213744838.9523 | 213744838.9523 | 4320044949.6176 | Core commodity use tab
Natural gas | therms/y | 29588294.2696 | 29588294.2696 | 29588294.2696 | 29254078.5799 | 29254078.5799 | 24175855.0457 | 24175855.0457 | 23428380.0144 | 23428380.0144 | 23117842.8071 | 20500994.3871 | 20115359.9245 | 20115359.9245 | 20021371.6537 | 6752672.3299 | 7178624.458 | 7178624.458 | 7160234.6155 | 7160234.6155 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 460260365.9333 | Core commodity use tab
Water | CCF/y | 261286.0572 | 280053.8811 | 280053.8811 | 299698.9983 | 299698.9983 | 268615.2808 | 268615.2808 | 259012.4952 | 259012.4952 | 258565.4864 | 222406.5794 | 218915.0463 | 218915.0463 | 218142.4149 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 6229798.8211 | Core commodity use tab
Carbon | tons CO2-eq/y | 198922.1024 | 198922.1024 | 198922.1024 | 196675.1703 | 196675.1703 | 162534.2735 | 162534.2735 | 157508.9988 | 157508.9988 | 155421.2572 | 137828.1853 | 135235.5648 | 135235.5648 | 134603.6816 | 45398.2161 | 48261.8922 | 48261.8922 | 48138.2573 | 48138.2573 | 48018.5761 | 48018.5761 | 48018.5761 | 48018.5761 | 48018.5761 | 48018.5761 | 47898.6045 | 47898.6045 | 47898.6045 | 47898.6045 | 47898.6045 | 3094330.4402
Energy | (MMBtu/y) | Year 2054: 1441756.1813 | 60766029.9614
Option 1B
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 40881228.9773 | 40881228.9773 | 40881228.9773 | 38703970.8292 | 38703970.8292 | 144979354.6901 | 144979354.6901 | 139241066.597 | 139241066.597 | 139836397.949 | 221776033.222 | 220343199.3193 | 220343199.3193 | 219988679.5091 | 353949831.9547 | 402745531.6841 | 402745531.6841 | 402247666.1524 | 402247666.1524 | 401217333.9438 | 401217333.9438 | 401217333.9438 | 401217333.9438 | 401217333.9438 | 401217333.9438 | 400062049.1548 | 400062049.1548 | 400062049.1548 | 400062049.1548 | 400062049.1548 | 8162330457.5477 | Core commodity use tab
Natural gas | therms/y | 28820560.6063 | 28820560.6063 | 28820560.6063 | 28545341.2881 | 28545341.2881 | 21374251.3975 | 21374251.3975 | 20706876.4783 | 20706876.4783 | 20396339.271 | 16670601.866 | 16331380.6211 | 16331380.6211 | 16248856.7698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313693179.2957 | Core commodity use tab
Water | CCF/y | 261286.0572 | 280053.8811 | 280053.8811 | 299698.9983 | 299698.9983 | 268615.2808 | 268615.2808 | 259012.4952 | 259012.4952 | 258565.4864 | 222406.5794 | 218915.0463 | 218915.0463 | 218142.4149 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 6229798.8211 | Core commodity use tab
Carbon | tons CO2-eq/y | 193760.629 | 193760.629 | 193760.629 | 191910.3295 | 191910.3295 | 143699.0921 | 143699.0921 | 139212.3306 | 139212.3306 | 137124.5889 | 112076.4563 | 109795.8719 | 109795.8719 | 109241.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2108959.2444 |  | Natural Gas Use
Energy | (MMBtu/y) | Year 2054: 1365011.7117 | 59219189.4507
Option 1C
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 30759933.5382 | 30759933.5382 | 30759933.5382 | 29646735.0007 | 29646735.0007 | 106387961.5804 | 106387961.5804 | 102094360.5373 | 102094360.5373 | 102689691.8893 | 166606299.678 | 165942244.0495 | 165942244.0495 | 165794496.7125 | 260074297.7538 | 303633784.1218 | 303633784.1218 | 303390755.7758 | 303390755.7758 | 302681496.4296 | 302681496.4296 | 302681496.4296 | 302681496.4296 | 302681496.4296 | 302681496.4296 | 301848063.4395 | 301848063.4395 | 301848063.4395 | 301848063.4395 | 301848063.4395 | 6134965564.5544 | Core commodity use tab
Natural gas | therms/y | 28820560.6063 | 28820560.6063 | 28820560.6063 | 28545341.2881 | 28545341.2881 | 21374251.3975 | 21374251.3975 | 20706876.4783 | 20706876.4783 | 20396339.271 | 16670601.866 | 16331380.6211 | 16331380.6211 | 16248856.7698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313693179.2957 | Core commodity use tab
Water | CCF/y | 261286.0572 | 280053.8811 | 280053.8811 | 299698.9983 | 299698.9983 | 268615.2808 | 268615.2808 | 259012.4952 | 259012.4952 | 258565.4864 | 222406.5794 | 218915.0463 | 218915.0463 | 218142.4149 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 6229798.8211 | Core commodity use tab
Carbon | tons CO2-eq/y | 193760.629 | 193760.629 | 193760.629 | 191910.3295 | 191910.3295 | 143699.0921 | 143699.0921 | 139212.3306 | 139212.3306 | 137124.5889 | 112076.4563 | 109795.8719 | 109795.8719 | 109241.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2108959.2444
Energy | (MMBtu/y) | Year 2054: 1029905.5925 | 52301820.4358
Option 2
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2865758.5346 | Core commodity use tab
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 13231647.3488 | 12967671.8734 | 12967671.8734 | 12750842.004 | 12750842.004 | 12218669.9351 | 12218669.9351 | 12043802.7946 | 12043802.7946 | 11773318.0441 | 11773318.0441 | 11708380.6081 | 11708380.6081 | 12487631.4977 | 12487631.4977 | 12455788.7491 | 12455788.7491 | 12421037.4882 | 12421037.4882 | 12421037.4882 | 12421037.4882 | 12421037.4882 | 12421037.4882 | 12386201.9193 | 12386201.9193 | 12386201.9193 | 12386201.9193 | 12386201.9193 | 409018847.4528 | Core commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 168874.6507 | 189729.7682 | 189729.7682 | 210959.0178 | 210959.0178 | 204508.3938 | 204508.3938 | 206948.1803 | 206948.1803 | 205098.1932 | 205098.1932 | 204677.115 | 204677.115 | 235460.8406 | 235460.8406 | 235394.2329 | 235394.2329 | 234839.6335 | 234839.6335 | 234839.6335 | 234839.6335 | 234839.6335 | 234839.6335 | 234104.8346 | 234104.8346 | 234104.8346 | 234104.8346 | 234104.8346 | 6709629.6913 | Core commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 88956.3651 | 87181.658 | 87181.658 | 85723.9108 | 85723.9108 | 82146.118 | 82146.118 | 80970.4862 | 80970.4862 | 79152.0172 | 79152.0172 | 78715.4428 | 78715.4428 | 83954.3466 | 83954.3466 | 83740.2678 | 83740.2678 | 83506.635 | 83506.635 | 83506.635 | 83506.635 | 83506.635 | 83506.635 | 83272.4355 | 83272.4355 | 83272.4355 | 83272.4355 | 83272.4355 | 2749833.7114
Energy | (MMBtu/y) | Year 2054: 1238620.1919 | 40911662.7134
Option 6
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 213515470.0081 | 229465787.0952 | 229465787.0952 | 234269958.3774 | 234269958.3774 | 223444695.6728 | 223444695.6728 | 223635944.0528 | 223635944.0528 | 221889618.5061 | 221889618.5061 | 221508563.4493 | 221508563.4493 | 263195564.8147 | 263195564.8147 | 263082526.4769 | 263082526.4769 | 262508797.6753 | 262508797.6753 | 262508797.6753 | 262508797.6753 | 262508797.6753 | 262508797.6753 | 261801987.1032 | 261801987.1032 | 261801987.1032 | 261801987.1032 | 261801987.1032 | 6861429267.0007 | Enhancement commodity use tab | Water Use
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 8313140.9881 | 8136703.1927 | 8136703.1927 | 8007874.6843 | 8007874.6843 | 7626218.3373 | 7626218.3373 | 7500809.3616 | 7500809.3616 | 7325257.4422 | 7325257.4422 | 7286849.5097 | 7286849.5097 | 7806338.3018 | 7806338.3018 | 7786557.2136 | 7786557.2136 | 7761634.7495 | 7761634.7495 | 7761634.7495 | 7761634.7495 | 7761634.7495 | 7761634.7495 | 7736651.8224 | 7736651.8224 | 7736651.8224 | 7736651.8224 | 7736651.8224 | 279037179.2497 | Enhancement commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 168824.4131 | 189680.5968 | 189680.5968 | 210910.6249 | 210910.6249 | 204462.3073 | 204462.3073 | 206902.8517 | 206902.8517 | 205053.9254 | 205053.9254 | 204633.0794 | 204633.0794 | 235413.6656 | 235413.6656 | 235347.1775 | 235347.1775 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | 6708321.2295 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 55889.2469 | 54703.0556 | 54703.0556 | 53836.9415 | 53836.9415 | 51271.0659 | 51271.0659 | 50427.9413 | 50427.9413 | 49247.7058 | 49247.7058 | 48989.4893 | 48989.4893 | 52482.0124 | 52482.0124 | 52349.0241 | 52349.0241 | 52181.4704 | 52181.4704 | 52181.4704 | 52181.4704 | 52181.4704 | 52181.4704 | 52013.5102 | 52013.5102 | 52013.5102 | 52013.5102 | 52013.5102 | 1875966.9561
Energy | (MMBtu/y) | Year 2054: 1666933.5622 | 51314914.584
Option 8A
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 2865758.5346 | 20224353.7995 | 20224353.7995 | 111765402.8853 | 111765402.8853 | 104086948.9321 | 104086948.9321 | 104086948.9321 | 234810349.112 | 229501819.8474 | 229501819.8474 | 228289943.0458 | 419973326.8202 | 475809134.2023 | 475809134.2023 | 475157337.7931 | 475157337.7931 | 473904820.3144 | 473904820.3144 | 473904820.3144 | 473904820.3144 | 473904820.3144 | 473904820.3144 | 472517574.295 | 472517574.295 | 472517574.295 | 472517574.295 | 472517574.295 | 9031998873.2595 | Core commodity use tab
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 31258877.2831 | 30779136.7519 | 30779136.7519 | 26715362.4366 | 26715362.4366 | 26000353.613 | 26000353.613 | 25689816.4057 | 17369500.8413 | 17280686.4306 | 17280686.4306 | 17265421.5508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355652449.1113 | Core commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 297204.7035 | 315431.1862 | 315431.1862 | 313904.4008 | 313904.4008 | 303318.1024 | 303318.1024 | 303961.4703 | 261875.2983 | 259512.3752 | 259512.3752 | 259003.1864 | 204633.0794 | 235413.6656 | 235413.6656 | 235347.1775 | 235347.1775 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | 7807219.9121 | Core commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 210153.432 | 206928.1364 | 206928.1364 | 179607.3817 | 179607.3817 | 174800.3773 | 174800.3773 | 172712.6357 | 116775.1542 | 116178.0549 | 116178.0549 | 116075.4291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2391051.4154
Energy | (MMBtu/y) | Year 2054: 1612229.9635 | 66382425.0667
Option 8B
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 2865758.5346 | 20224353.7995 | 20224353.7995 | 86109327.4072 | 86109327.4072 | 80106481.391 | 80106481.391 | 80106481.391 | 163130613.3908 | 160341438.8159 | 160341438.8159 | 159711102.4474 | 288547578.9388 | 335013877.191 | 335013877.191 | 334718852.8418 | 334718852.8418 | 333915837.3705 | 333915837.3705 | 333915837.3705 | 333915837.3705 | 333915837.3705 | 333915837.3705 | 332979183.8695 | 332979183.8695 | 332979183.8695 | 332979183.8695 | 332979183.8695 | 6398646899.7003 | Core commodity use tab
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 31258877.2831 | 30779136.7519 | 30779136.7519 | 26715362.4366 | 26715362.4366 | 26000353.613 | 26000353.613 | 25689816.4057 | 17369500.8413 | 17280686.4306 | 17280686.4306 | 17265421.5508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355652449.1113 | Core commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 297204.7035 | 315431.1862 | 315431.1862 | 313904.4008 | 313904.4008 | 303318.1024 | 303318.1024 | 303961.4703 | 261875.2983 | 259512.3752 | 259512.3752 | 259003.1864 | 204633.0794 | 235413.6656 | 235413.6656 | 235347.1775 | 235347.1775 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | 7807219.9121 | Core commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 210153.432 | 206928.1364 | 206928.1364 | 179607.3817 | 179607.3817 | 174800.3773 | 174800.3773 | 172712.6357 | 116775.1542 | 116178.0549 | 116178.0549 | 116075.4291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2391051.4154
Energy | (MMBtu/y) | Year 2054: 1136124.9754 | 57397428.1329
Option 10A
Item | Unit | Year 2025: Year | Total | Source | Carbon Emissions
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 47837563.6783 | 168997147.2443 | 186004902.5418 | 186004902.5418 | 192394342.8968 | 192394342.8968 | 181395211.2003 | 181395211.2003 | 181654503.7405 | 181654503.7405 | 180550748.0195 | 180550748.0195 | 180464890.1038 | 180464890.1038 | 221514950.2935 | 221514950.2935 | 221514950.2935 | 221514950.2935 | 220926206.1473 | 220926206.1473 | 220926206.1473 | 220926206.1473 | 220926206.1473 | 220926206.1473 | 220199433.4649 | 220199433.4649 | 220199433.4649 | 220199433.4649 | 220199433.4649 | 5734378113.3108 | Enhancement commodity use tab
Natural gas | therms/y | 31258877.2831 | 30649221.0674 | 18613368.2003 | 18347752.44 | 18347752.44 | 18113313.827 | 18113313.827 | 17604058.2587 | 17604058.2587 | 17436721.2821 | 17436721.2821 | 17159265.9771 | 17159265.9771 | 17088878.8445 | 17088878.8445 | 17874338.0026 | 17874338.0026 | 17840779.9266 | 17840779.9266 | 17807525.1315 | 17807525.1315 | 17807525.1315 | 17807525.1315 | 17807525.1315 | 17807525.1315 | 17774189.6589 | 17774189.6589 | 17774189.6589 | 17774189.6589 | 17774189.6589 | 559167782.7516 | Enhancement commodity use tab
Water | CCF/y | 278436.8796 | 263270.7656 | 229722.3986 | 249312.6806 | 249312.6806 | 269580.3854 | 269580.3854 | 260455.0602 | 260455.0602 | 262015.963 | 262015.963 | 258895.1272 | 258895.1272 | 258186.9184 | 258186.9184 | 292697.9137 | 292697.9137 | 292485.954 | 292485.954 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 290846.8117 | 290846.8117 | 290846.8117 | 290846.8117 | 290846.8117 | 8263464.2736 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 206054.7132 | 125137.6744 | 123351.9397 | 123351.9397 | 121775.8089 | 121775.8089 | 118352.0837 | 118352.0837 | 117227.0772 | 117227.0772 | 115361.7452 | 115361.7452 | 114888.5325 | 114888.5325 | 120169.1744 | 120169.1744 | 119943.5634 | 119943.5634 | 119719.9915 | 119719.9915 | 119719.9915 | 119719.9915 | 119719.9915 | 119719.9915 | 119495.8771 | 119495.8771 | 119495.8771 | 119495.8771 | 119495.8771 | 3759285.0034
Energy | (MMBtu/y) | Year 2054: 2528739.4329 | 75482476.3978
Option 11A
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 1011886.4347 | 3877644.9693 | 79202580.4606 | 155992314.02 | 155992314.02 | 157184785.3623 | 157184785.3623 | 147426684.6333 | 147426684.6333 | 147081317.9435 | 147081317.9435 | 146298589.3386 | 146298589.3386 | 146271369.2751 | 146271369.2751 | 181155964.4902 | 181155964.4902 | 181155964.4902 | 181155964.4902 | 180685017.7339 | 180685017.7339 | 180685017.7339 | 180685017.7339 | 180685017.7339 | 180685017.7339 | 180116495.5311 | 180116495.5311 | 180116495.5311 | 180116495.5311 | 180116495.5311 | 4593918675.0296 | Core commodity use tab
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 25498951.0122 | 7433987.211 | 7433987.211 | 7304772.2299 | 7304772.2299 | 7032160.5534 | 7032160.5534 | 6942582.7136 | 6942582.7136 | 6791488.9426 | 6791488.9426 | 6752672.3299 | 6752672.3299 | 7178624.458 | 7178624.458 | 7160234.6155 | 7160234.6155 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 279687288.3566 | Core commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 234601.0887 | 134952.5224 | 134952.5224 | 148916.8093 | 148916.8093 | 144579.4907 | 144579.4907 | 146193.8892 | 146193.8892 | 144821.9214 | 144821.9214 | 144483.6016 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 5010462.419 | Core commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 171429.4477 | 49978.696 | 49978.696 | 49109.9837 | 49109.9837 | 47277.2154 | 47277.2154 | 46674.9836 | 46674.9836 | 45659.1802 | 45659.1802 | 45398.2161 | 45398.2161 | 48261.8922 | 48261.8922 | 48138.2573 | 48138.2573 | 48018.5761 | 48018.5761 | 48018.5761 | 48018.5761 | 48018.5761 | 48018.5761 | 47898.6045 | 47898.6045 | 47898.6045 | 47898.6045 | 47898.6045 | 1880337.6396
Energy | (MMBtu/y) | Year 2054: 1327016.2735 | 43643179.3549
Option 11B
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 1011886.4347 | 3877644.9693 | 145235755.5254 | 352865229.8041 | 352865229.8041 | 350530524.1432 | 350530524.1432 | 333626369.804 | 333626369.804 | 330851127.089 | 330851127.089 | 325993668.9907 | 325993668.9907 | 324918032.9792 | 324918032.9792 | 370368508.6459 | 370368508.6459 | 369870643.1142 | 369870643.1142 | 368928302.9244 | 368928302.9244 | 368928302.9244 | 368928302.9244 | 368928302.9244 | 368928302.9244 | 367889998.8936 | 367889998.8936 | 367889998.8936 | 367889998.8936 | 367889998.8936 | 9721193308.0838 | Core commodity use tab
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 22981692.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85499446.8954 | Core commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 234601.0887 | 134952.5224 | 134952.5224 | 148916.8093 | 148916.8093 | 144579.4907 | 144579.4907 | 146193.8892 | 146193.8892 | 144821.9214 | 144821.9214 | 144483.6016 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 5010462.419 | Core commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 154505.9175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574812.7815
Energy | (MMBtu/y) | Year 2054: 1255240.6762 | 41718656.2567
Option 11C
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 1011886.4347 | 3877644.9693 | 107335630.5308 | 248041141.1728 | 248041141.1728 | 247366116.4245 | 247366116.4245 | 235378791.1501 | 235378791.1501 | 234219175.9536 | 234219175.9536 | 231623330.3926 | 231623330.3926 | 231042498.7782 | 231042498.7782 | 269800467.9235 | 269800467.9235 | 269557439.5775 | 269557439.5775 | 268936172.2502 | 268936172.2502 | 268936172.2502 | 268936172.2502 | 268936172.2502 | 268936172.2502 | 268219720.0183 | 268219720.0183 | 268219720.0183 | 268219720.0183 | 268219720.0183 | 7000998718.2728 | Core commodity use tab
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 22981692.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85499446.8954 | Core commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 234601.0887 | 134952.5224 | 134952.5224 | 148916.8093 | 148916.8093 | 144579.4907 | 144579.4907 | 146193.8892 | 146193.8892 | 144821.9214 | 144821.9214 | 144483.6016 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 5010462.419 | Core commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 154505.9175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574812.7815
Energy | (MMBtu/y) | Year 2054: 915165.6847 | 32437352.3163
Option 12
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 226071828.5231 | 239769654.1745 | 239769654.1745 | 243575227.4488 | 243575227.4488 | 230569005.5643 | 230569005.5643 | 233025410.5537 | 233025410.5537 | 230656887.8044 | 230656887.8044 | 230089670.127 | 230089670.127 | 263403700.6801 | 263403700.6801 | 263792946.3144 | 263792946.3144 | 263083686.9682 | 263083686.9682 | 263083686.9682 | 263083686.9682 | 263083686.9682 | 263083686.9682 | 262832276.4728 | 262832276.4728 | 262832276.4728 | 262832276.4728 | 262832276.4728 | 6991366096.5652 | Enhancement commodity use tab
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 2565274.1089 | 2565274.1089 | 2565274.1089 | 2565274.1089 | 2565274.1089 | 2565274.1089 | 2565274.1089 | 2346467.9582 | 2346467.9582 | 2314068.5606 | 2314068.5606 | 2310160.1223 | 2310160.1223 | 3182974.7107 | 3182974.7107 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3097709.5353 | 3097709.5353 | 3097709.5353 | 3097709.5353 | 3097709.5353 | 141400949.8387 | Enhancement commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 145239.9156 | 159041.2633 | 159041.2633 | 177058.6462 | 177058.6462 | 172721.3277 | 172721.3277 | 173191.8538 | 173191.8538 | 171584.8106 | 171584.8106 | 171211.4885 | 171211.4885 | 203880.0341 | 203880.0341 | 203668.0744 | 203668.0744 | 203295.9317 | 203295.9317 | 203295.9317 | 203295.9317 | 203295.9317 | 203295.9317 | 202386.0489 | 202386.0489 | 202386.0489 | 202386.0489 | 202386.0489 | 5817302.3302 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 17246.3378 | 17246.3378 | 17246.3378 | 17246.3378 | 17246.3378 | 17246.3378 | 17246.3378 | 15775.3041 | 15775.3041 | 15557.4829 | 15557.4829 | 15531.2065 | 15531.2065 | 21399.139 | 21399.139 | 21118.9482 | 21118.9482 | 21118.9482 | 21118.9482 | 21118.9482 | 21118.9482 | 21118.9482 | 21118.9482 | 20825.9012 | 20825.9012 | 20825.9012 | 20825.9012 | 20825.9012 | 950638.5858
Energy | (MMBtu/y) | Year 2054: 1206554.6809 | 37994636.1053
Enhancements | [33 empty] | Graphs: All Options | Graphs: New Phasing
Option 0 | [33 empty] | Electricity Use | Electricity Use
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 0 | 0 | 0 | 0 | 16120936.062 | 16120936.062 | 15369930.1899 | 15369930.1899 | 15619355.1103 | 15619355.1103 | 14493235.7149 | 14493235.7149 | 14406600.0831 | 14406600.0831 | 56453362.9932 | 56453362.9932 | 56453362.9932 | 56453362.9932 | 55851163.2254 | 55851163.2254 | 55851163.2254 | 55851163.2254 | 55851163.2254 | 55851163.2254 | 55108147.0515 | 55108147.0515 | 55108147.0515 | 55108147.0515 | 55108147.0515 | 988481280.9034 | Enhancement commodity use tab
Natural gas | therms/y | 32306018.9957 | 32306018.9957 | 30132827.3313 | 29794799.6281 | 29794799.6281 | 27449723.8437 | 27449723.8437 | 20733939.1692 | 20733939.1692 | 20515133.0185 | 20515133.0185 | 20165629.3435 | 20165629.3435 | 20079479.1879 | 20079479.1879 | 21078142.0574 | 21078142.0574 | 21036465.613 | 21036465.613 | 20992982.3742 | 20992982.3742 | 20992982.3742 | 20992982.3742 | 20992982.3742 | 20992982.3742 | 20949393.6433 | 20949393.6433 | 20949393.6433 | 20949393.6433 | 20949393.6433 | 687156351.5073 | Enhancement commodity use tab
Water | CCF/y | 244502.9416 | 263270.7656 | 242776.8462 | 262367.1282 | 262367.1282 | 270875.8345 | 270875.8345 | 260455.0602 | 260455.0602 | 262015.963 | 262015.963 | 258895.1272 | 258895.1272 | 258186.9184 | 258186.9184 | 292697.9137 | 292697.9137 | 292485.954 | 292485.954 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 290846.8117 | 290846.8117 | 290846.8117 | 290846.8117 | 290846.8117 | 8271284.5766 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 217193.3657 | 217193.3657 | 202582.9981 | 200310.4379 | 200310.4379 | 184544.4934 | 184544.4934 | 139394.273 | 139394.273 | 137923.2393 | 137923.2393 | 135573.5261 | 135573.5261 | 134994.3386 | 134994.3386 | 141708.3491 | 141708.3491 | 141428.1583 | 141428.1583 | 141135.8205 | 141135.8205 | 141135.8205 | 141135.8205 | 141135.8205 | 141135.8205 | 140842.7735 | 140842.7735 | 140842.7735 | 140842.7735 | 140842.7735 | 4619752.1512
Energy | (MMBtu/y) | Year 2054: 2282968.3621 | 72088333.2812
Option 1A
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 20641256.4616 | 20641256.4616 | 20641256.4616 | 20057383.2552 | 20057383.2552 | 70900161.0628 | 70900161.0628 | 67248921.2517 | 67248921.2517 | 67846283.4621 | 120965437.0548 | 120791014.575 | 120791014.575 | 120747962.1804 | 175303168.2507 | 214989280.6885 | 214989280.6885 | 214989280.6885 | 214989280.6885 | 214430341.9133 | 214430341.9133 | 214430341.9133 | 214430341.9133 | 214430341.9133 | 214430341.9133 | 213744838.9523 | 213744838.9523 | 213744838.9523 | 213744838.9523 | 213744838.9523 | 4320044949.6176 | Enhancement commodity use tab
Natural gas | therms/y | 29588294.2696 | 29588294.2696 | 29588294.2696 | 29254078.5799 | 29254078.5799 | 24175855.0457 | 24175855.0457 | 23428380.0144 | 23428380.0144 | 23117842.8071 | 20500994.3871 | 20115359.9245 | 20115359.9245 | 20021371.6537 | 6752672.3299 | 7178624.458 | 7178624.458 | 7160234.6155 | 7160234.6155 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 460260365.9333 | Enhancement commodity use tab
Water | CCF/y | 261286.0572 | 280053.8811 | 280053.8811 | 299698.9983 | 299698.9983 | 268615.2808 | 268615.2808 | 259012.4952 | 259012.4952 | 258565.4864 | 222406.5794 | 218915.0463 | 218915.0463 | 218142.4149 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 6229798.8211 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 198922.1024 | 198922.1024 | 198922.1024 | 196675.1703 | 196675.1703 | 162534.2735 | 162534.2735 | 157508.9988 | 157508.9988 | 155421.2572 | 137828.1853 | 135235.5648 | 135235.5648 | 134603.6816 | 45398.2161 | 48261.8922 | 48261.8922 | 48138.2573 | 48138.2573 | 48018.5761 | 48018.5761 | 48018.5761 | 48018.5761 | 48018.5761 | 48018.5761 | 47898.6045 | 47898.6045 | 47898.6045 | 47898.6045 | 47898.6045 | 3094330.4402
Energy | (MMBtu/y) | Year 2054: 1441756.1813 | 60766029.9614
Option 1B
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 40881228.9773 | 40881228.9773 | 40881228.9773 | 38703970.8292 | 38703970.8292 | 144979354.6901 | 144979354.6901 | 139241066.597 | 139241066.597 | 139836397.949 | 221776033.222 | 220343199.3193 | 220343199.3193 | 219988679.5091 | 353949831.9547 | 402745531.6841 | 402745531.6841 | 402247666.1524 | 402247666.1524 | 401217333.9438 | 401217333.9438 | 401217333.9438 | 401217333.9438 | 401217333.9438 | 401217333.9438 | 400062049.1548 | 400062049.1548 | 400062049.1548 | 400062049.1548 | 400062049.1548 | 8162330457.5477 | Enhancement commodity use tab
Natural gas | therms/y | 28820560.6063 | 28820560.6063 | 28820560.6063 | 28545341.2881 | 28545341.2881 | 21374251.3975 | 21374251.3975 | 20706876.4783 | 20706876.4783 | 20396339.271 | 16670601.866 | 16331380.6211 | 16331380.6211 | 16248856.7698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313693179.2957 | Enhancement commodity use tab
Water | CCF/y | 261286.0572 | 280053.8811 | 280053.8811 | 299698.9983 | 299698.9983 | 268615.2808 | 268615.2808 | 259012.4952 | 259012.4952 | 258565.4864 | 222406.5794 | 218915.0463 | 218915.0463 | 218142.4149 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 6229798.8211 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 193760.629 | 193760.629 | 193760.629 | 191910.3295 | 191910.3295 | 143699.0921 | 143699.0921 | 139212.3306 | 139212.3306 | 137124.5889 | 112076.4563 | 109795.8719 | 109795.8719 | 109241.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2108959.2444 |  | Natural Gas Use | Natural Gas Use
Energy | (MMBtu/y) | Year 2054: 1365011.7117 | 59219189.4507
Option 1C
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 30759933.5382 | 30759933.5382 | 30759933.5382 | 29646735.0007 | 29646735.0007 | 106387961.5804 | 106387961.5804 | 102094360.5373 | 102094360.5373 | 102689691.8893 | 166606299.678 | 165942244.0495 | 165942244.0495 | 165794496.7125 | 260074297.7538 | 303633784.1218 | 303633784.1218 | 303390755.7758 | 303390755.7758 | 302681496.4296 | 302681496.4296 | 302681496.4296 | 302681496.4296 | 302681496.4296 | 302681496.4296 | 301848063.4395 | 301848063.4395 | 301848063.4395 | 301848063.4395 | 301848063.4395 | 6134965564.5544 | Enhancement commodity use tab
Natural gas | therms/y | 28820560.6063 | 28820560.6063 | 28820560.6063 | 28545341.2881 | 28545341.2881 | 21374251.3975 | 21374251.3975 | 20706876.4783 | 20706876.4783 | 20396339.271 | 16670601.866 | 16331380.6211 | 16331380.6211 | 16248856.7698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 313693179.2957 | Enhancement commodity use tab
Water | CCF/y | 261286.0572 | 280053.8811 | 280053.8811 | 299698.9983 | 299698.9983 | 268615.2808 | 268615.2808 | 259012.4952 | 259012.4952 | 258565.4864 | 222406.5794 | 218915.0463 | 218915.0463 | 218142.4149 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 6229798.8211 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 193760.629 | 193760.629 | 193760.629 | 191910.3295 | 191910.3295 | 143699.0921 | 143699.0921 | 139212.3306 | 139212.3306 | 137124.5889 | 112076.4563 | 109795.8719 | 109795.8719 | 109241.0641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2108959.2444
Energy | (MMBtu/y) | Year 2054: 1029905.5925 | 52301820.4358
Option 2
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2865758.5346 | Enhancement commodity use tab
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 13231647.3488 | 12967671.8734 | 12967671.8734 | 12750842.004 | 12750842.004 | 12218669.9351 | 12218669.9351 | 12043802.7946 | 12043802.7946 | 11773318.0441 | 11773318.0441 | 11708380.6081 | 11708380.6081 | 12487631.4977 | 12487631.4977 | 12455788.7491 | 12455788.7491 | 12421037.4882 | 12421037.4882 | 12421037.4882 | 12421037.4882 | 12421037.4882 | 12421037.4882 | 12386201.9193 | 12386201.9193 | 12386201.9193 | 12386201.9193 | 12386201.9193 | 409018847.4528 | Enhancement commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 168874.6507 | 189729.7682 | 189729.7682 | 210959.0178 | 210959.0178 | 204508.3938 | 204508.3938 | 206948.1803 | 206948.1803 | 205098.1932 | 205098.1932 | 204677.115 | 204677.115 | 235460.8406 | 235460.8406 | 235394.2329 | 235394.2329 | 234839.6335 | 234839.6335 | 234839.6335 | 234839.6335 | 234839.6335 | 234839.6335 | 234104.8346 | 234104.8346 | 234104.8346 | 234104.8346 | 234104.8346 | 6709629.6913 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 88956.3651 | 87181.658 | 87181.658 | 85723.9108 | 85723.9108 | 82146.118 | 82146.118 | 80970.4862 | 80970.4862 | 79152.0172 | 79152.0172 | 78715.4428 | 78715.4428 | 83954.3466 | 83954.3466 | 83740.2678 | 83740.2678 | 83506.635 | 83506.635 | 83506.635 | 83506.635 | 83506.635 | 83506.635 | 83272.4355 | 83272.4355 | 83272.4355 | 83272.4355 | 83272.4355 | 2749833.7114
Energy | (MMBtu/y) | Year 2054: 1238620.1919 | 40911662.7134
Option 6
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 213515470.0081 | 229465787.0952 | 229465787.0952 | 234269958.3774 | 234269958.3774 | 223444695.6728 | 223444695.6728 | 223635944.0528 | 223635944.0528 | 221889618.5061 | 221889618.5061 | 221508563.4493 | 221508563.4493 | 263195564.8147 | 263195564.8147 | 263082526.4769 | 263082526.4769 | 262508797.6753 | 262508797.6753 | 262508797.6753 | 262508797.6753 | 262508797.6753 | 262508797.6753 | 261801987.1032 | 261801987.1032 | 261801987.1032 | 261801987.1032 | 261801987.1032 | 6861429267.0007 | Enhancement commodity use tab | Water Use | Water Use
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 8313140.9881 | 8136703.1927 | 8136703.1927 | 8007874.6843 | 8007874.6843 | 7626218.3373 | 7626218.3373 | 7500809.3616 | 7500809.3616 | 7325257.4422 | 7325257.4422 | 7286849.5097 | 7286849.5097 | 7806338.3018 | 7806338.3018 | 7786557.2136 | 7786557.2136 | 7761634.7495 | 7761634.7495 | 7761634.7495 | 7761634.7495 | 7761634.7495 | 7761634.7495 | 7736651.8224 | 7736651.8224 | 7736651.8224 | 7736651.8224 | 7736651.8224 | 279037179.2497 | Enhancement commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 168824.4131 | 189680.5968 | 189680.5968 | 210910.6249 | 210910.6249 | 204462.3073 | 204462.3073 | 206902.8517 | 206902.8517 | 205053.9254 | 205053.9254 | 204633.0794 | 204633.0794 | 235413.6656 | 235413.6656 | 235347.1775 | 235347.1775 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | 6708321.2295 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 55889.2469 | 54703.0556 | 54703.0556 | 53836.9415 | 53836.9415 | 51271.0659 | 51271.0659 | 50427.9413 | 50427.9413 | 49247.7058 | 49247.7058 | 48989.4893 | 48989.4893 | 52482.0124 | 52482.0124 | 52349.0241 | 52349.0241 | 52181.4704 | 52181.4704 | 52181.4704 | 52181.4704 | 52181.4704 | 52181.4704 | 52013.5102 | 52013.5102 | 52013.5102 | 52013.5102 | 52013.5102 | 1875966.9561
Energy | (MMBtu/y) | Year 2054: 1666933.5622 | 51314914.584
Option 8A
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 2865758.5346 | 20224353.7995 | 20224353.7995 | 111765402.8853 | 111765402.8853 | 104086948.9321 | 104086948.9321 | 104086948.9321 | 234810349.112 | 229501819.8474 | 229501819.8474 | 228289943.0458 | 419973326.8202 | 475809134.2023 | 475809134.2023 | 475157337.7931 | 475157337.7931 | 473904820.3144 | 473904820.3144 | 473904820.3144 | 473904820.3144 | 473904820.3144 | 473904820.3144 | 472517574.295 | 472517574.295 | 472517574.295 | 472517574.295 | 472517574.295 | 9031998873.2595 | Enhancement commodity use tab
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 31258877.2831 | 30779136.7519 | 30779136.7519 | 26715362.4366 | 26715362.4366 | 26000353.613 | 26000353.613 | 25689816.4057 | 17369500.8413 | 17280686.4306 | 17280686.4306 | 17265421.5508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355652449.1113 | Enhancement commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 297204.7035 | 315431.1862 | 315431.1862 | 313904.4008 | 313904.4008 | 303318.1024 | 303318.1024 | 303961.4703 | 261875.2983 | 259512.3752 | 259512.3752 | 259003.1864 | 204633.0794 | 235413.6656 | 235413.6656 | 235347.1775 | 235347.1775 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | 7807219.9121 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 210153.432 | 206928.1364 | 206928.1364 | 179607.3817 | 179607.3817 | 174800.3773 | 174800.3773 | 172712.6357 | 116775.1542 | 116178.0549 | 116178.0549 | 116075.4291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2391051.4154
Energy | (MMBtu/y) | Year 2054: 1612229.9635 | 66382425.0667
Option 8B
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 0 | 0 | 8385065.6062 | 8385065.6062 | 73500800.17 | 73500800.17 | 67497954.1538 | 67497954.1538 | 67497954.1538 | 150522086.1535 | 147732911.5787 | 147732911.5787 | 147102575.2102 | 275939051.7016 | 320894511.191 | 320894511.191 | 320599486.8418 | 320599486.8418 | 319796471.3705 | 319796471.3705 | 319796471.3705 | 319796471.3705 | 319796471.3705 | 319796471.3705 | 318859817.8695 | 318859817.8695 | 318859817.8695 | 318859817.8695 | 318859817.8695 | 6031361043.8722 | Enhancement commodity use tab
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 31258877.2831 | 30779136.7519 | 30779136.7519 | 26715362.4366 | 26715362.4366 | 26000353.613 | 26000353.613 | 25689816.4057 | 17369500.8413 | 17280686.4306 | 17280686.4306 | 17265421.5508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355652449.1113 | Enhancement commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 297204.7035 | 315431.1862 | 315431.1862 | 313904.4008 | 313904.4008 | 303318.1024 | 303318.1024 | 303961.4703 | 261875.2983 | 259512.3752 | 259512.3752 | 259003.1864 | 204633.0794 | 235413.6656 | 235413.6656 | 235347.1775 | 235347.1775 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234792.7287 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | 234058.0808 | 7807219.9121 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 210153.432 | 206928.1364 | 206928.1364 | 179607.3817 | 179607.3817 | 174800.3773 | 174800.3773 | 172712.6357 | 116775.1542 | 116178.0549 | 116178.0549 | 116075.4291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2391051.4154
Energy | (MMBtu/y) | Year 2054: 1087949.6986 | 56144248.7928
Option 10A | [33 empty] | Carbon Emissions | Carbon Emissions
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 47837563.6783 | 168997147.2443 | 186004902.5418 | 186004902.5418 | 192394342.8968 | 192394342.8968 | 181395211.2003 | 181395211.2003 | 181654503.7405 | 181654503.7405 | 180550748.0195 | 180550748.0195 | 180464890.1038 | 180464890.1038 | 221514950.2935 | 221514950.2935 | 221514950.2935 | 221514950.2935 | 220926206.1473 | 220926206.1473 | 220926206.1473 | 220926206.1473 | 220926206.1473 | 220926206.1473 | 220199433.4649 | 220199433.4649 | 220199433.4649 | 220199433.4649 | 220199433.4649 | 5734378113.3108 | Enhancement commodity use tab
Natural gas | therms/y | 31258877.2831 | 30649221.0674 | 18613368.2003 | 18347752.44 | 18347752.44 | 18113313.827 | 18113313.827 | 17604058.2587 | 17604058.2587 | 17436721.2821 | 17436721.2821 | 17159265.9771 | 17159265.9771 | 17088878.8445 | 17088878.8445 | 17874338.0026 | 17874338.0026 | 17840779.9266 | 17840779.9266 | 17807525.1315 | 17807525.1315 | 17807525.1315 | 17807525.1315 | 17807525.1315 | 17807525.1315 | 17774189.6589 | 17774189.6589 | 17774189.6589 | 17774189.6589 | 17774189.6589 | 559167782.7516 | Enhancement commodity use tab
Water | CCF/y | 278436.8796 | 263270.7656 | 229722.3986 | 249312.6806 | 249312.6806 | 269580.3854 | 269580.3854 | 260455.0602 | 260455.0602 | 262015.963 | 262015.963 | 258895.1272 | 258895.1272 | 258186.9184 | 258186.9184 | 292697.9137 | 292697.9137 | 292485.954 | 292485.954 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 291756.6944 | 290846.8117 | 290846.8117 | 290846.8117 | 290846.8117 | 290846.8117 | 8263464.2736 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 206054.7132 | 125137.6744 | 123351.9397 | 123351.9397 | 121775.8089 | 121775.8089 | 118352.0837 | 118352.0837 | 117227.0772 | 117227.0772 | 115361.7452 | 115361.7452 | 114888.5325 | 114888.5325 | 120169.1744 | 120169.1744 | 119943.5634 | 119943.5634 | 119719.9915 | 119719.9915 | 119719.9915 | 119719.9915 | 119719.9915 | 119719.9915 | 119495.8771 | 119495.8771 | 119495.8771 | 119495.8771 | 119495.8771 | 3759285.0034
Energy | (MMBtu/y) | Year 2054: 2528739.4329 | 75482476.3978
Option 11A
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 1011886.4347 | 3877644.9693 | 79202580.4606 | 155992314.02 | 155992314.02 | 157184785.3623 | 157184785.3623 | 147426684.6333 | 147426684.6333 | 147081317.9435 | 147081317.9435 | 146298589.3386 | 146298589.3386 | 146271369.2751 | 146271369.2751 | 181155964.4902 | 181155964.4902 | 181155964.4902 | 181155964.4902 | 180685017.7339 | 180685017.7339 | 180685017.7339 | 180685017.7339 | 180685017.7339 | 180685017.7339 | 180116495.5311 | 180116495.5311 | 180116495.5311 | 180116495.5311 | 180116495.5311 | 4593918675.0296 | Enhancement commodity use tab
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 25498951.0122 | 7433987.211 | 7433987.211 | 7304772.2299 | 7304772.2299 | 7032160.5534 | 7032160.5534 | 6942582.7136 | 6942582.7136 | 6791488.9426 | 6791488.9426 | 6752672.3299 | 6752672.3299 | 7178624.458 | 7178624.458 | 7160234.6155 | 7160234.6155 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7142432.8554 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 7124587.9075 | 279687288.3566 | Enhancement commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 234601.0887 | 134952.5224 | 134952.5224 | 148916.8093 | 148916.8093 | 144579.4907 | 144579.4907 | 146193.8892 | 146193.8892 | 144821.9214 | 144821.9214 | 144483.6016 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 5010462.419 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 171429.4477 | 49978.696 | 49978.696 | 49109.9837 | 49109.9837 | 47277.2154 | 47277.2154 | 46674.9836 | 46674.9836 | 45659.1802 | 45659.1802 | 45398.2161 | 45398.2161 | 48261.8922 | 48261.8922 | 48138.2573 | 48138.2573 | 48018.5761 | 48018.5761 | 48018.5761 | 48018.5761 | 48018.5761 | 48018.5761 | 47898.6045 | 47898.6045 | 47898.6045 | 47898.6045 | 47898.6045 | 1880337.6396
Energy | (MMBtu/y) | Year 2054: 1327016.2735 | 43643179.3549
Option 11B
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 1011886.4347 | 3877644.9693 | 145235755.5254 | 352865229.8041 | 352865229.8041 | 350530524.1432 | 350530524.1432 | 333626369.804 | 333626369.804 | 330851127.089 | 330851127.089 | 325993668.9907 | 325993668.9907 | 324918032.9792 | 324918032.9792 | 370368508.6459 | 370368508.6459 | 369870643.1142 | 369870643.1142 | 368928302.9244 | 368928302.9244 | 368928302.9244 | 368928302.9244 | 368928302.9244 | 368928302.9244 | 367889998.8936 | 367889998.8936 | 367889998.8936 | 367889998.8936 | 367889998.8936 | 9721193308.0838 | Enhancement commodity use tab
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 22981692.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85499446.8954 | Enhancement commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 234601.0887 | 134952.5224 | 134952.5224 | 148916.8093 | 148916.8093 | 144579.4907 | 144579.4907 | 146193.8892 | 146193.8892 | 144821.9214 | 144821.9214 | 144483.6016 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 5010462.419 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 154505.9175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574812.7815
Energy | (MMBtu/y) | Year 2054: 1255240.6762 | 41718656.2567
Option 11C
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 1011886.4347 | 3877644.9693 | 107335630.5308 | 248041141.1728 | 248041141.1728 | 247366116.4245 | 247366116.4245 | 235378791.1501 | 235378791.1501 | 234219175.9536 | 234219175.9536 | 231623330.3926 | 231623330.3926 | 231042498.7782 | 231042498.7782 | 269800467.9235 | 269800467.9235 | 269557439.5775 | 269557439.5775 | 268936172.2502 | 268936172.2502 | 268936172.2502 | 268936172.2502 | 268936172.2502 | 268936172.2502 | 268219720.0183 | 268219720.0183 | 268219720.0183 | 268219720.0183 | 268219720.0183 | 7000998718.2728 | Enhancement commodity use tab
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 22981692.3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85499446.8954 | Enhancement commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 234601.0887 | 134952.5224 | 134952.5224 | 148916.8093 | 148916.8093 | 144579.4907 | 144579.4907 | 146193.8892 | 146193.8892 | 144821.9214 | 144821.9214 | 144483.6016 | 144483.6016 | 165316.1734 | 165316.1734 | 165249.6853 | 165249.6853 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164877.5426 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 164385.2611 | 5010462.419 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 154505.9175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574812.7815
Energy | (MMBtu/y) | Year 2054: 915165.6847 | 32437352.3163
Option 12
Item | Unit | Year 2025: Year | Total | Source
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
Electricity | kWh/y | 0 | 2865758.5346 | 226071828.5231 | 239769654.1745 | 239769654.1745 | 243575227.4488 | 243575227.4488 | 230569005.5643 | 230569005.5643 | 233025410.5537 | 233025410.5537 | 230656887.8044 | 230656887.8044 | 230089670.127 | 230089670.127 | 263403700.6801 | 263403700.6801 | 263792946.3144 | 263792946.3144 | 263083686.9682 | 263083686.9682 | 263083686.9682 | 263083686.9682 | 263083686.9682 | 263083686.9682 | 262832276.4728 | 262832276.4728 | 262832276.4728 | 262832276.4728 | 262832276.4728 | 6991366096.5652 | Enhancement commodity use tab
Natural gas | therms/y | 31258877.2831 | 31258877.2831 | 2565274.1089 | 2565274.1089 | 2565274.1089 | 2565274.1089 | 2565274.1089 | 2565274.1089 | 2565274.1089 | 2346467.9582 | 2346467.9582 | 2314068.5606 | 2314068.5606 | 2310160.1223 | 2310160.1223 | 3182974.7107 | 3182974.7107 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3141298.2662 | 3097709.5353 | 3097709.5353 | 3097709.5353 | 3097709.5353 | 3097709.5353 | 141400949.8387 | Enhancement commodity use tab
Water | CCF/y | 278436.8796 | 297204.7035 | 145239.9156 | 159041.2633 | 159041.2633 | 177058.6462 | 177058.6462 | 172721.3277 | 172721.3277 | 173191.8538 | 173191.8538 | 171584.8106 | 171584.8106 | 171211.4885 | 171211.4885 | 203880.0341 | 203880.0341 | 203668.0744 | 203668.0744 | 203295.9317 | 203295.9317 | 203295.9317 | 203295.9317 | 203295.9317 | 203295.9317 | 202386.0489 | 202386.0489 | 202386.0489 | 202386.0489 | 202386.0489 | 5817302.3302 | Enhancement commodity use tab
Carbon | tons CO2-eq/y | 210153.432 | 210153.432 | 17246.3378 | 17246.3378 | 17246.3378 | 17246.3378 | 17246.3378 | 17246.3378 | 17246.3378 | 15775.3041 | 15775.3041 | 15557.4829 | 15557.4829 | 15531.2065 | 15531.2065 | 21399.139 | 21399.139 | 21118.9482 | 21118.9482 | 21118.9482 | 21118.9482 | 21118.9482 | 21118.9482 | 21118.9482 | 21118.9482 | 20825.9012 | 20825.9012 | 20825.9012 | 20825.9012 | 20825.9012 | 950638.5858
Energy | (MMBtu/y) | Year 2054: 1206554.6809 | 37994636.1053
Comparison Charts |  | Year 2039: Graphs: All Options |  | Graphs: New Phasing
Final Commodities Usage
|  | 0 | 1a | 1c | 1c E | 2 | 6 | 8b | 8b E | 10a | 11a | 11c | 11c E | 12
Electricity | kWh/y | Year 2025: 55851163.2254; Year 2026: 214430341.9133; Year 2027: 302681496.4296; Year 2028: 302681496.4296; Year 2029: 0; Year 2030: 262508797.6753; Year 2031: 333915837.3705; Year 2032: 319796471.3705; Year 2033: 220926206.1473; Year 2034: 180685017.7339; Year 2035: 268936172.2502; Year 2036: 268936172.2502; Year 2037: 263083686.9682
Natural gas | therms/y | Year 2025: 20992982.3742; Year 2026: 7142432.8554; Year 2027: 0; Year 2028: 0; Year 2029: 12421037.4882; Year 2030: 7761634.7495; Year 2031: 0; Year 2032: 0; Year 2033: 17807525.1315; Year 2034: 7142432.8554; Year 2035: 0; Year 2036: 0; Year 2037: 3141298.2662
Water | CCF/y | Year 2025: 291756.6944; Year 2026: 164877.5426; Year 2027: 164877.5426; Year 2028: 164877.5426; Year 2029: 234839.6335; Year 2030: 234792.7287; Year 2031: 234792.7287; Year 2032: 234792.7287; Year 2033: 291756.6944; Year 2034: 164877.5426; Year 2035: 164877.5426; Year 2036: 164877.5426; Year 2037: 203295.9317
Carbon | Tons CO2-eq/y | Year 2025: 141135.8205; Year 2026: 48018.5761; Year 2027: 0; Year 2028: 0; Year 2029: 83506.635; Year 2030: 52181.4704; Year 2031: 0; Year 2032: 0; Year 2033: 119719.9915; Year 2034: 48018.5761; Year 2035: 0; Year 2036: 0; Year 2037: 21118.9482
Final Commodities Cost ($/y)
|  | 0 | 1a | 1c | 1c E | 2 | 6 | 8b | 8b E | 10a | 11a | 11c | 11c E | 12
Electricity | $/y, 2045 | Year 2025: 17022268.6012; Year 2026: 65353891.7634; Year 2027: 92251001.3272; Year 2028: 83025901.1945; Year 2029: 0; Year 2030: 80007201.3929; Year 2031: 101770576.3973; Year 2032: 97467288.3966; Year 2033: 67333695.5741; Year 2034: 55069021.4215; Year 2035: 81966130.9853; Year 2036: 73769517.8868; Year 2037: 72164174.0832
Natural gas | $/y, 2045 | Year 2025: 55874025.1058; Year 2026: 19009994.1765; Year 2027: 0; Year 2028: 0; Year 2029: 33059302.7747; Year 2030: 20658035.4865; Year 2031: 0; Year 2032: 0; Year 2033: 47395748.1854; Year 2034: 19009994.1765; Year 2035: 0; Year 2036: 0; Year 2037: 8360745.275
Water | $/y, 2045 | Year 2025: 14537553.3491; Year 2026: 8215462.1205; Year 2027: 8215462.1205; Year 2028: 8215462.1205; Year 2029: 11701509.3936; Year 2030: 11699172.2366; Year 2031: 11699172.2366; Year 2032: 11699172.2366; Year 2033: 14537553.3491; Year 2034: 8215462.1205; Year 2035: 8215462.1205; Year 2036: 8215462.1205; Year 2037: 10129760.5461
Carbon | $/y, 2045 | Year 2025: 25171573.5865; Year 2026: 8564113.0451; Year 2027: 0; Year 2028: 0; Year 2029: 14893408.3582; Year 2030: 9306565.2495; Year 2031: 0; Year 2032: 0; Year 2033: 21352060.4768; Year 2034: 8564113.0451; Year 2035: 0; Year 2036: 0; Year 2037: 3766564.4193
Total | $/y, 2045 | Year 2025: 112605420.6426; Year 2026: 101143461.1055; Year 2027: 100466463.4477; Year 2028: 91241363.315; Year 2029: 59654220.5265; Year 2030: 121670974.3655; Year 2031: 113469748.6339; Year 2032: 109166460.6332; Year 2033: 150619057.5854; Year 2034: 90858590.7636; Year 2035: 90181593.1058; Year 2036: 81984980.0073; Year 2037: 94421244.3235
Final O&M Cost
|  | 0 | 1a | 1c | 1c E | 2 | 6 | 8b | 8b E | 10a | 11a | 11c | 11c E | 12
O&M | USD/y, 2045 | Year 2025: 15273000; Year 2026: 16363400; Year 2027: 16857500; Year 2028: 18160800; Year 2029: 20138100; Year 2030: 13274900; Year 2031: 13455500; Year 2032: 16941300; Year 2033: 9066700; Year 2034: 15640900; Year 2035: 17140000; Year 2036: 17140000; Year 2037: 28554600
O&M | $M USD/y, 2045 | Year 2025: 15.273; Year 2026: 16.3634; Year 2027: 16.8575; Year 2028: 18.1608; Year 2029: 20.1381; Year 2030: 13.2749; Year 2031: 13.4555; Year 2032: 16.9413; Year 2033: 9.0667; Year 2034: 15.6409; Year 2035: 17.14; Year 2036: 17.14; Year 2037: 28.5546
Final Commodities Cost ($M USD/y)
|  | 0 | 1a | 1c | 1c E | 2 | 6 | 8b | 8b E | 10a | 11a | 11c | 11c E | 12
Electricity | $M USD/y, 2045 | Year 2025: 17.0223; Year 2026: 65.3539; Year 2027: 92.251; Year 2028: 83.0259; Year 2029: 0; Year 2030: 80.0072; Year 2031: 101.7706; Year 2032: 97.4673; Year 2033: 67.3337; Year 2034: 55.069; Year 2035: 81.9661; Year 2036: 73.7695; Year 2037: 72.1642
Natural gas | $M USD/y, 2045 | Year 2025: 55.874; Year 2026: 19.01; Year 2027: 0; Year 2028: 0; Year 2029: 33.0593; Year 2030: 20.658; Year 2031: 0; Year 2032: 0; Year 2033: 47.3957; Year 2034: 19.01; Year 2035: 0; Year 2036: 0; Year 2037: 8.3607
Water | $M USD/y, 2045 | Year 2025: 14.5376; Year 2026: 8.2155; Year 2027: 8.2155; Year 2028: 8.2155; Year 2029: 11.7015; Year 2030: 11.6992; Year 2031: 11.6992; Year 2032: 11.6992; Year 2033: 14.5376; Year 2034: 8.2155; Year 2035: 8.2155; Year 2036: 8.2155; Year 2037: 10.1298
Carbon | $M USD/y, 2045 | Year 2025: 25.1716; Year 2026: 8.5641; Year 2027: 0; Year 2028: 0; Year 2029: 14.8934; Year 2030: 9.3066; Year 2031: 0; Year 2032: 0; Year 2033: 21.3521; Year 2034: 8.5641; Year 2035: 0; Year 2036: 0; Year 2037: 3.7666
Total | $M USD/y, 2045 | Year 2025: 112.6054; Year 2026: 101.1435; Year 2027: 100.4665; Year 2028: 91.2414; Year 2029: 59.6542; Year 2030: 121.671; Year 2031: 113.4697; Year 2032: 109.1665; Year 2033: 150.6191; Year 2034: 90.8586; Year 2035: 90.1816; Year 2036: 81.985; Year 2037: 94.4212
Final Operating Cost ($M USD/y)
|  | 0 | 1a | 1c | 1c E | 2 | 6 | 8b | 8b E | 10a | 11a | 11c | 11c E | 12
Electricity | $M USD/y, 2045 | Year 2025: 17.0223; Year 2026: 65.3539; Year 2027: 92.251; Year 2028: 83.0259; Year 2029: 0; Year 2030: 80.0072; Year 2031: 101.7706; Year 2032: 97.4673; Year 2033: 67.3337; Year 2034: 55.069; Year 2035: 81.9661; Year 2036: 73.7695; Year 2037: 72.1642
Natural gas | $M USD/y, 2045 | Year 2025: 55.874; Year 2026: 19.01; Year 2027: 0; Year 2028: 0; Year 2029: 33.0593; Year 2030: 20.658; Year 2031: 0; Year 2032: 0; Year 2033: 47.3957; Year 2034: 19.01; Year 2035: 0; Year 2036: 0; Year 2037: 8.3607
Water | $M USD/y, 2045 | Year 2025: 14.5376; Year 2026: 8.2155; Year 2027: 8.2155; Year 2028: 8.2155; Year 2029: 11.7015; Year 2030: 11.6992; Year 2031: 11.6992; Year 2032: 11.6992; Year 2033: 14.5376; Year 2034: 8.2155; Year 2035: 8.2155; Year 2036: 8.2155; Year 2037: 10.1298
Carbon | $M USD/y, 2045 | Year 2025: 25.1716; Year 2026: 8.5641; Year 2027: 0; Year 2028: 0; Year 2029: 14.8934; Year 2030: 9.3066; Year 2031: 0; Year 2032: 0; Year 2033: 21.3521; Year 2034: 8.5641; Year 2035: 0; Year 2036: 0; Year 2037: 3.7666
O&M | $M USD/y, 2045 | Year 2025: 15.273; Year 2026: 16.3634; Year 2027: 16.8575; Year 2028: 18.1608; Year 2029: 20.1381; Year 2030: 13.2749; Year 2031: 13.4555; Year 2032: 16.9413; Year 2033: 9.0667; Year 2034: 15.6409; Year 2035: 17.14; Year 2036: 17.14; Year 2037: 28.5546
Total | $M USD/y, 2045 | Year 2025: 127.8784; Year 2026: 117.5069; Year 2027: 117.324; Year 2028: 109.4022; Year 2029: 79.7923; Year 2030: 134.9459; Year 2031: 126.9252; Year 2032: 126.1078; Year 2033: 159.6858; Year 2034: 106.4995; Year 2035: 107.3216; Year 2036: 99.125; Year 2037: 122.9758
Formatted for Report |  | Year 2039: Graphs: All Options |  | Graphs: New Phasing
Final Commodities Use
|  | 0 | 1a | 1c E | 2 | 6 | 8b E | 10a | 11a | 11c E | 12
Electricity | kWh/y | Year 2025: 55851163.2254; Year 2026: 214430341.9133; Year 2027: 302681496.4296; Year 2028: 0; Year 2029: 262508797.6753; Year 2030: 319796471.3705; Year 2031: 220926206.1473; Year 2032: 180685017.7339; Year 2033: 268936172.2502; Year 2034: 263083686.9682
Natural gas | therms/y | Year 2025: 20992982.3742; Year 2026: 7142432.8554; Year 2027: 0; Year 2028: 12421037.4882; Year 2029: 7761634.7495; Year 2030: 0; Year 2031: 17807525.1315; Year 2032: 7142432.8554; Year 2033: 0; Year 2034: 3141298.2662
Water | CCF/y | Year 2025: 291756.6944; Year 2026: 164877.5426; Year 2027: 164877.5426; Year 2028: 234839.6335; Year 2029: 234792.7287; Year 2030: 234792.7287; Year 2031: 291756.6944; Year 2032: 164877.5426; Year 2033: 164877.5426; Year 2034: 203295.9317
Carbon | Tons CO2-eq/y | Year 2025: 141135.8205; Year 2026: 48018.5761; Year 2027: 0; Year 2028: 83506.635; Year 2029: 52181.4704; Year 2030: 0; Year 2031: 119719.9915; Year 2032: 48018.5761; Year 2033: 0; Year 2034: 21118.9482
Final Commodities Use
|  | 0 | 1a | 1c E | 2 | 6 | 8b E | 10a | 11a | 11c E | 12
Electricity | MWh/y x1000 | Year 2025: 55.8512; Year 2026: 214.4303; Year 2027: 302.6815; Year 2028: 0; Year 2029: 262.5088; Year 2030: 319.7965; Year 2031: 220.9262; Year 2032: 180.685; Year 2033: 268.9362; Year 2034: 263.0837
Natural gas | therms/y x1000 | Year 2025: 20992.9824; Year 2026: 7142.4329; Year 2027: 0; Year 2028: 12421.0375; Year 2029: 7761.6347; Year 2030: 0; Year 2031: 17807.5251; Year 2032: 7142.4329; Year 2033: 0; Year 2034: 3141.2983
Water | CCF/y x1000 | Year 2025: 291.7567; Year 2026: 164.8775; Year 2027: 164.8775; Year 2028: 234.8396; Year 2029: 234.7927; Year 2030: 234.7927; Year 2031: 291.7567; Year 2032: 164.8775; Year 2033: 164.8775; Year 2034: 203.2959
Carbon | Tons CO2-eq/y x1000 | Year 2025: 141.1358; Year 2026: 48.0186; Year 2027: 0; Year 2028: 83.5066; Year 2029: 52.1815; Year 2030: 0; Year 2031: 119.72; Year 2032: 48.0186; Year 2033: 0; Year 2034: 21.1189
Final Commodities Cost
|  | 0 | 1a | 1c E | 2 | 6 | 8b E | 10a | 11a | 11c E | 12
Electricity | $M USD/y, 2045 | Year 2025: 17.0223; Year 2026: 65.3539; Year 2027: 83.0259; Year 2028: 0; Year 2029: 80.0072; Year 2030: 97.4673; Year 2031: 67.3337; Year 2032: 55.069; Year 2033: 73.7695; Year 2034: 72.1642
Natural gas | $M USD/y, 2045 | Year 2025: 55.874; Year 2026: 19.01; Year 2027: 0; Year 2028: 33.0593; Year 2029: 20.658; Year 2030: 0; Year 2031: 47.3957; Year 2032: 19.01; Year 2033: 0; Year 2034: 8.3607
Water | $M USD/y, 2045 | Year 2025: 14.5376; Year 2026: 8.2155; Year 2027: 8.2155; Year 2028: 11.7015; Year 2029: 11.6992; Year 2030: 11.6992; Year 2031: 14.5376; Year 2032: 8.2155; Year 2033: 8.2155; Year 2034: 10.1298
Carbon | $M USD/y, 2045 | Year 2025: 25.1716; Year 2026: 8.5641; Year 2027: 0; Year 2028: 14.8934; Year 2029: 9.3066; Year 2030: 0; Year 2031: 21.3521; Year 2032: 8.5641; Year 2033: 0; Year 2034: 3.7666
Total | $M USD/y, 2045 | Year 2025: 112.6054; Year 2026: 101.1435; Year 2027: 91.2414; Year 2028: 59.6542; Year 2029: 121.671; Year 2030: 109.1665; Year 2031: 150.6191; Year 2032: 90.8586; Year 2033: 81.985; Year 2034: 94.4212
Final Operating Cost
|  | 0 | 1a | 1c E | 2 | 6 | 8b E | 10a | 11a | 11c E | 12
Electricity | $M USD/y, 2045 | Year 2025: 17.0223; Year 2026: 65.3539; Year 2027: 83.0259; Year 2028: 0; Year 2029: 80.0072; Year 2030: 97.4673; Year 2031: 67.3337; Year 2032: 55.069; Year 2033: 73.7695; Year 2034: 72.1642
Natural gas | $M USD/y, 2045 | Year 2025: 55.874; Year 2026: 19.01; Year 2027: 0; Year 2028: 33.0593; Year 2029: 20.658; Year 2030: 0; Year 2031: 47.3957; Year 2032: 19.01; Year 2033: 0; Year 2034: 8.3607
Water | $M USD/y, 2045 | Year 2025: 14.5376; Year 2026: 8.2155; Year 2027: 8.2155; Year 2028: 11.7015; Year 2029: 11.6992; Year 2030: 11.6992; Year 2031: 14.5376; Year 2032: 8.2155; Year 2033: 8.2155; Year 2034: 10.1298
Carbon | $M USD/y, 2045 | Year 2025: 25.1716; Year 2026: 8.5641; Year 2027: 0; Year 2028: 14.8934; Year 2029: 9.3066; Year 2030: 0; Year 2031: 21.3521; Year 2032: 8.5641; Year 2033: 0; Year 2034: 3.7666
O&M | $M USD/y, 2045 | Year 2025: 15.273; Year 2026: 16.3634; Year 2027: 18.1608; Year 2028: 20.1381; Year 2029: 13.2749; Year 2030: 16.9413; Year 2031: 9.0667; Year 2032: 15.6409; Year 2033: 17.14; Year 2034: 28.5546
Total | $M USD/y, 2045 | Year 2025: 127.8784; Year 2026: 117.5069; Year 2027: 109.4022; Year 2028: 79.7923; Year 2029: 134.9459; Year 2030: 126.1078; Year 2031: 159.6858; Year 2032: 106.4995; Year 2033: 99.125; Year 2034: 122.9758
Difference vs Baseline
|  | 0 | 1a | 1c E | 2 | 6 | 8b E | 10a | 11a | 11c E | 12
Electricity | MWh/y x1000 | Year 2025: 0; Year 2026: 158.5792; Year 2027: 246.8303; Year 2028: -55.8512; Year 2029: 206.6576; Year 2030: 263.9453; Year 2031: 165.075; Year 2032: 124.8339; Year 2033: 213.085; Year 2034: 207.2325
Natural gas | therms/y x1000 | Year 2025: 0; Year 2026: -13850.5495; Year 2027: -20992.9824; Year 2028: -8571.9449; Year 2029: -13231.3476; Year 2030: -20992.9824; Year 2031: -3185.4572; Year 2032: -13850.5495; Year 2033: -20992.9824; Year 2034: -17851.6841
Water | CCF/y x1000 | Year 2025: 0; Year 2026: -126.8792; Year 2027: -126.8792; Year 2028: -56.9171; Year 2029: -56.964; Year 2030: -56.964; Year 2031: 0; Year 2032: -126.8792; Year 2033: -126.8792; Year 2034: -88.4608
Carbon | Tons CO2-eq/y x1000 | Year 2025: 0; Year 2026: -93.1172; Year 2027: -141.1358; Year 2028: -57.6292; Year 2029: -88.9544; Year 2030: -141.1358; Year 2031: -21.4158; Year 2032: -93.1172; Year 2033: -141.1358; Year 2034: -120.0169
Commodities cost | $M USD/y, 2045 | Year 2025: 0; Year 2026: -11.462; Year 2027: -21.3641; Year 2028: -52.9512; Year 2029: 9.0656; Year 2030: -3.439; Year 2031: 38.0136; Year 2032: -21.7468; Year 2033: -30.6204; Year 2034: -18.1842
Operating cost | $M USD/y, 2045 | Year 2025: 0; Year 2026: -10.3716; Year 2027: -18.4763; Year 2028: -48.0861; Year 2029: 7.0675; Year 2030: -1.7707; Year 2031: 31.8073; Year 2032: -21.3789; Year 2033: -28.7534; Year 2034: -4.9026
Capital cost | NPV first cost ($M USD) | Year 2025: 0; Year 2026: 139; Year 2027: 165; Year 2028: 118; Year 2029: 59; Year 2030: 155; Year 2031: -17; Year 2032: 166; Year 2033: 198; Year 2034: 141
Life cycle cost | NPV 30-year life cycle cost ($M USD) | Year 2025: 0; Year 2026: 69; Year 2027: 29; Year 2028: -378; Year 2029: 127; Year 2030: 62; Year 2031: 310; Year 2032: 6; Year 2033: -81; Year 2034: 90
Old vs New Phasing
Carbon Emsisions (tons CO2-eq/y) | [32 empty] | Carbon Emissions
Option | Phasing | Year 2025: Year | Total
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
2 | New | 210153.432 | 210153.432 | 88956.3651 | 87181.658 | 87181.658 | 85723.9108 | 85723.9108 | 82146.118 | 82146.118 | 80970.4862 | 80970.4862 | 79152.0172 | 79152.0172 | 78715.4428 | 78715.4428 | 83954.3466 | 83954.3466 | 83740.2678 | 83740.2678 | 83506.635 | 83506.635 | 83506.635 | 83506.635 | 83506.635 | 83506.635 | 83272.4355 | 83272.4355 | 83272.4355 | 83272.4355 | 83272.4355 | 2749833.7114
11c-E | New | 210153.432 | 210153.432 | 154505.9175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 574812.7815
2 | Old | 210153.432 | 210426.196 | 210409.6897 | 208613.8201 | 208484.7311 | 193318.8833 | 193318.8833 | 187640.9666 | 187640.9666 | 185553.225 | 159399.0695 | 157319.7349 | 157319.7349 | 156838.3245 | 78715.4428 | 83954.3466 | 83954.3466 | 83740.2678 | 83740.2678 | 83506.635 | 83506.635 | 83506.635 | 83506.635 | 83506.635 | 83506.635 | 83272.4355 | 83272.4355 | 83272.4355 | 83272.4355 | 83272.4355 | 3226866.3663
11c-E | Old | 210255.2568 | 210522.5078 | 210500.1731 | 208698.16 | 208562.6123 | 184896.7289 | 184369.4012 | 178714.9183 | 178181.1544 | 175537.8544 | 121190.3672 | 119363.6587 | 118163.8931 | 116816.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1983454.5243
Note on B331: [线程批注] 你的Excel版本可读取此线程批注; 但如果在更新版本的Excel中打开文件，则对批注所作的任何改动都将被删除。了解详细信息: https://go.microsoft.com/fwlink/?linkid=870924 注释: From cost estimate
Note on B332: [线程批注] 你的Excel版本可读取此线程批注; 但如果在更新版本的Excel中打开文件，则对批注所作的任何改动都将被删除。了解详细信息: https://go.microsoft.com/fwlink/?linkid=870924 注释: From cost estimate